## TOTAL ABS
NAME OF WORK: REDEVELOPMENT OF ARMY COLLEGE OF MEDICAL SCIENCES CAMPUS (ACMS)
TOTAL ABSTRACT BILL OF QUANTITIES (BOQ)
S/N | DISCRIPTION | AMOUNT IN FIGURE (INR) | AMOUNT IN WORDS (INR)
1 | AUDITORIUM
2 | BOYS HOSTEL (BUILDING NO. 1, 2, 3 & 4)
3 | GIRLS HOSTEL & FACULY BLOCKS (BUILDING NO. 1, 2, 3 & 4)
4 | UTILITY & ACADEMIC BLOCK AND RENOVATION OF LABORATORIES
5 | TOTAL

## GENABS AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
ABSTRACT BILL OF QUANTITIES (BOQ)
NAME OF PROJECT: AUDITORIUM
S/N | DISCRIPTION | AMOUNT (INR) IN FIGURE | AMOUNT (INR) IN WORDS
1 | BASEMENT 1
2 | BASEMENT 2
3 | GROUND FLOOR
4 | FIRST FLOOR
5 | SECOND FLOOR
6 | TERRACE FLOOR
1 | SANITATION
2 | ELECTRICAL
3 | CCTV SYSTEM
4 | MISCELLENIOUS
5 | HVAC
6 | SUB TOTAL
7 | DEVIATIONS UPTO 3%
8 | TOTAL |  |  | 0

## BASEMENT 1 AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR BASEMENT 1
S/N | DESCRIPTION | NO. | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | EXCAVATION FOR BASEMENT AND FOUNDATION Excavation for foundations, substructures, basements, tanks, sumps, walls, chambers, manholes, trenches, poles, pits & general building works in all types of soils, vegetable earth, soft murum, running sand, shingle, turf clay, loam, peat, ash, shale, slag, chalk, garbage, muddy/ marshy/ slushy soil, marine clay, reclaimed land etc. for depths/lifts upto 6.0 M measured from the basement level, including dressing/ trimming the sides, levelling and ramming of bottoms, manual dewatering, removing rank vegetation, backfilling in layers not more than 200mm thickness, watering, consolidating, compacting to achieve not less then 97% Modified Proctor density conforming to relevant IS, stacking the selected material in measurable heaps for future use within owners space or disposing within an initial lead of 150 m as directed, loading, unloading, levelling excluding shoring, strutting etc. complete as directed by Engineer-in-Charge.
| Note: 1) The rate includes the dewatering the basement or any other excavated parts, 2) Keeping the site clean and shifting of all the excavated materials from the site, 3) Shuttering and centring etc. complete |  | 9075.275 | CuM
2 | FILLING IN PLINTH Filling in plinth, floors, trenches, pits with approved contractor's murum in layers not exceeding 200mm including breaking of clods, watering, consolidating each layer in filled up area by rolling and compacting with roller/ plate compactor as required to achieve not less than 97% modified proctor density conforming to relevant IS etc. complete as directed by Engineer In charge. The rate includes necessary soil testing charges at laboratory & field as per relevant I.S. codes, royalty, octroi and other taxes if any. (Note: Borrow areas selected by CONTRACTOR shall be got approved from Engineer In Charge, before executing the work) 1) The rate includes the royalty and other taxes if any. |  | 2722.5825 | CuM
3 | STONE RUBBLE SOILING Providing & Laying dry stone Rubble Soling with average 230 mm size hard stone set in regular lines, handpicked and interstices thoroughly filled with small chips including filling in with good quality murum brought from outside, compacting with iron rammers, watering, sand spreading 12mm thk. layer of grit on top etc complete as directed by Engineer In Charge. (Note: The rate includes the royalty and other taxes if any) |  | 1388 | CuM
4 | DISMANTLING BRICK WORK, STEEL WORKS, LANDSCAPE WORK ETC. Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 1 | 500 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete |  | 500 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. |  | 1352.5 | SqM
7 | M-20 PLAIN CEMENT CONCRETE M-20 grade plain cement concrete (cement content considered @ 260 kg/cum as per IS 456 table showing minimum cement content). |  | 324.6 | Cum
8 | READY MIX COCNRETE Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centring, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete.
Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.
| All works upto plinth level: Concrete of M25 grade with minimum cement content of 330 kg /cum |  | 713.9028 | Cum
9 | RCC SLAB Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete |  | 262.1 | Cum
10 | RCC WAIST SLAB Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete |  | 5.6 | Cum
11 | CENTERING AND SHUTTERING Cantering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. |  | 214.1708 | Sqm
12 | HYSD REINFORCEMENT Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. |  | 68712.1944 | Kg
13 | AREATED CEMENT BLOCK MASONRY Providing and fixing up to third and fourth level autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work. |  | 81 | Cum
14 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 50 | SqM
15 | INTERNAL PLASTER FOR ADDTIONAL WORKS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. |  | 276 | Sqm
16 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete |  | 25 | Sqm
17 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. |  | 250 | Sqm
SIZE: 600 X 600 (Avg.)
18 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. |  | 75 | Sqm
SIZE: 600 X 600 (Avg.)
19 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) |  | 75 | SqM
| SIZE: 800 X 800 (Avg.) |  | 75 | SqM
| SIZE: 600 X 1200 (Avg.) |  | 75 | SqM
20 | MS FABRICATION WORK Providing and fixing MS fabrication work for basement, ducts, etc. as directed by engineer incharge including epoxy treatment etc. complete. |  | 5000 | Kg
21 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws |  | 7.56 | SqM
22 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm |  | 6.48 | Cum
23 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. |  | 276 | Sqm
24 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. |  | 82.8 | Sqm
25 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. |  | 1 | No.s
26 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete |  | 1 | No
27 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). |  | 1 | No
28 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) |  | 50 | Sqm
29 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete |  | 25 | Sqm
30 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) |  | 4 | No
31 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge |  | 1.296 | Sqm
32 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge |  | 0.432 | Sqm
33 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. |  | 250 | Sqm
34 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete |  | 150 | Sqm
35 | EXTERNAL CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. |  | 50 | Sqm
36 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete |  | 250 | Sqm
37 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete |  | 250 | Sqm
Total

## BASEMENT 2 AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR BASEMENT 2
S/N | DESCRIPTION | NO. | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORD
1 | EXCAVATION FOR BASEMENT AND FOUNDATION Excavation for foundations, substructures, basements, tanks, sumps, walls, chambers, manholes, trenches, poles, pits & general building works in all types of soils, vegetable earth, soft murum, running sand, shingle, turf clay, loam, peat, ash, shale, slag, chalk, garbage, muddy/ marshy/ slushy soil, marine clay, reclaimed land etc. for depths/lifts upto 6.0 M measured from the basement level, including dressing/ trimming the sides, levelling and ramming of bottoms, manual dewatering, removing rank vegetation, backfilling in layers not more than 200mm thickness, watering, consolidating, compacting to achieve not less then 97% Modified Proctor density conforming to relevant IS, stacking the selected material in measurable heaps for future use within owners space or disposing within an initial lead of 150 m as directed, loading, unloading, levelling excluding shoring, strutting etc. complete as directed by Engineer-in-Charge.
| Note: 1) The rate includes the dewatering the basement or any other excavated parts, 2) Keeping the site clean and shifting of all the excavated materials from the site, 3) Shuttering and centring etc. complete |  | 8182.625 | CuM
2 | FILLING IN PLINTH Filling in plinth, floors, trenches, pits with approved contractor's murum in layers not exceeding 200mm including breaking of clods, watering, consolidating each layer in filled up area by rolling and compacting with roller/ plate compactor as required to achieve not less than 97% modified proctor density conforming to relevant IS etc. complete as directed by Engineer In charge. The rate includes necessary soil testing charges at laboratory & field as per relevant I.S. codes, royalty, octroi and other taxes if any. (Note: Borrow areas selected by CONTRACTOR shall be got approved from Engineer In Charge, before executing the work) 1) The rate includes the royalty and other taxes if any. |  | 2454.7875 | CuM
3 | STONE RUBBLE SOILING Providing & Laying dry stone Rubble Soling with average 230 mm size hard stone set in regular lines, handpicked and interstices thoroughly filled with small chips including filling in with good quality murum brought from outside, compacting with iron rammers, watering, sand spreading 12mm thk. layer of grit on top etc complete as directed by Engineer In Charge. (Note: The rate includes the royalty and other taxes if any) |  | 1388 | CuM
4 | DISMANTLING BRICK WORK, STEEL WORKS, LANDSCAPE WORK ETC. Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 1 | 500 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete |  | 500 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. |  | 1352.5 | SqM
7 | M-20 PLAIN CEMENT CONCRETE M-20 grade plain cement concrete (cement content considered @ 260 kg/cum as per IS 456 table showing minimum cement content). |  | 324.6 | Cum
8 | READY MIX COCNRETE Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centring, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete.
Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.
| All works upto plinth level: Concrete of M25 grade with minimum cement content of 330 kg /cum |  | 713.9028 | Cum
9 | RCC SLAB Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete |  | 8.708 | Cum
10 | RCC WAIST SLAB Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete |  | 14.6 | Cum
11 | CENTERING AND SHUTTERING Cantering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. |  | 214.1708 | Sqm
12 | HYSD REINFORCEMENT Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. |  | 50974.7544 | Kg
13 | AREATED CEMENT BLOCK MASONRY Providing and fixing up to third and fourth level autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work. |  | 81 | Cum
14 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 50 | SqM
15 | INTERNAL PLASTER FOR ADDTIONAL WORKS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. |  | 276 | Sqm
16 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete |  | 25 | Sqm
17 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. |  | 250 | Sqm
SIZE: 600 X 600 (Avg.)
18 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. |  | 75 | Sqm
SIZE: 600 X 600 (Avg.)
19 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) |  | 75 | SqM
| SIZE: 800 X 800 (Avg.) |  | 75 | SqM
| SIZE: 600 X 1200 (Avg.) |  | 75 | SqM
20 | MS FABRICATION WORK Providing and fixing MS fabrication work for basement, ducts, etc. as directed by engineer incharge including epoxy treatment etc. complete. |  | 5000 | Kg
21 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws |  | 7.56 | SqM
22 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm |  | 6.48 | Cum
23 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. |  | 276 | Sqm
24 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. |  | 82.8 | Sqm
25 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. |  | 1 | No.s
26 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete |  | 1 | No
27 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). |  | 1 | No
28 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) |  | 50 | Sqm
29 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete |  | 25 | Sqm
30 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) |  | 4 | No
31 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge |  | 1.296 | Sqm
32 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge |  | 0.432 | Sqm
33 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. |  | 250 | Sqm
34 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete |  | 150 | Sqm
35 | EXTERNAL CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. |  | 50 | Sqm
36 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete |  | 250 | Sqm
37 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete |  | 250 | Sqm
Total

## GF AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITOIRUM
BOQ FOR GROUND FLOOR
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 694 | Sqm
2 | READY MIX COCNRETE Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centring, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete.
Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.
| All works above plinth level upto floor V level Concrete of M25 grade with minimum cement content of 330 kg /cum | 189.7481 | Cum
| Concrete of M30 grade with minimum cement content of 350 kg /cum | 36.3178 | Cum
3 | RCC SLAB Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 70.5 | Cum
4 | RCC WAIST SLAB Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 5.6 | Cum
5 | CENTERING AND SHUTTERING Cantering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 390.5304 | Sqm
6 | HYSD REINFORCEMENT Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 18609.3642 | Kg
7 | AREATED CEMENT BLOCK MASONRY Providing and fixing up to third and fourth level autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work. | 83.52 | Cum
8 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 25 | Cum
9 | INTERNAL PLASTER FOR ADDTIONAL ITEMS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 1035.92 | Sqm
10 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 478 | Sqm
11 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | 889 | Sqm
12 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | 266.7 | Sqm
13 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 75 | Sqm
| SIZE: 800 X 800 (Avg.) | 75 | Sqm
| SIZE: 600 X 1200 (Avg.) | 75 | Sqm
14 | MS FABRICATION WORK FOR GLAZING WORKS AND STRUCTURAL SUPPORT Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 450 | Kg
15 | DOORS (WITHOUT FRAMES) Providing and fixing country teak wood single leaf, 2nd class partly panelled door as per drawings including iron oxidised fixtures and fastenings and finishing the wood work with one coat of primer etc.(excluding door frame) complete. | 23.1 | Sqm
16 | DOOR FRAMES Providing and fixing first quality wood door frame of sizes 125x 62mm , 75 x 50 mm or any other size with 12 mm rebate for door shutter including superior grade melamine polishing etc. The base & side touching the floor/partition to be applied with ant termite treatment. The rate shall be inclusive of fixing necessary hardware for fixing the frame to partition etc. complete | 9.24 | Cum
17 | MAKING PAINT SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 1035.92 | Sqm
18 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 310.776 | Sqm
19 | DUCO PAINT Providing and applying Duco paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) etc. complete. | 310.776 | Sqm
20 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 310.776 | Sqm
21 | TEXTURE PAINT Providing and applying texture paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 155.388 | Sqm
22 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete.
| Three Seat | 124 | No.s
| Two Seat | 18 | No.s
23 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete | 416 | No.s
24 | CABINATES/LOCKERS Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 56 | No.s
25 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 150 | Sqm
26 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | Sqm
27 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 8 | Sqm
28 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 6 | No.s
29 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 6 | No.s
30 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 4 | No.s
31 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 2.16 | Sqm
32 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 20 | Sqm
33 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. | 250 | Sqm
34 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete | 150 | Sqm
35 | ENTRANCE PORTCH Providing and fixing of entrance porch by water proofing in bitumen with tile finish on top surface (as per water proofing specifications), replacement of old drainage with new drainage system, including painting, re concreting the floor etc. complete | 2 | No.s
36 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 250 | Sqm
37 | EXTERNAL GLAZING WORK Providing and fixing external glazing in 12 mm glass in St. Gobin or equivalent with one side reflective UV protective coating in cluding all the necessary This include scaffolding, providing necessary finish, labor etc. complete | 250 | Sqm
38 | CEILING & WALL PANELLING : MULTI-BOX CONTINUOUS SYSTEM Providing and fixing Multi-Box Continuous metal ceiling system with 2", 4", 6" and 8' panels with ceiling suspenders, and all necessary support of same brand of available or custom colors as pe drawings or engineer incharge or approved sample etc. complete. | 75 | Sqm
39 | METAL CLIP IN CEILING Providing and fixing Gl Clip in Metal Ceiling System of 600x600 mm module which includes providing and fixing 'C' wall angle of size 20x30x20 mm made of 0.5 mm thick pre painted steel along the perimeter of the room with help of nylon sleeves and wooden screws at 300 mm center to centre, suspending the main C carrier of size 10x38x10 mm made of G.I steel 0.7 mm thick from the soffit with help of soffit cleat 37x27x25x1.6 mm, rawl plugs of size 38x12 mm and C carrier suspension clip and main carrier bracket at 1000 mm c/c. Inverted triangle shaped Spring Tee having height of 24 mm and width of 34 mm made of Gl steel 0.45 mm thick is then fixed to the main C carrier and in direction perpendicular to it at 600 mm centers with help of suspension brackets. Wherever the main C carrier and spring T have to join, C carrier and spring T connectors have to be used. All sections to be galvanized @ 120 gms/sqm (both side inclusive), fixing with clip in tiles into spring T with : | 663 | Sqm
GI Metal Ceiling Clip in plain Bevelled edge global white color tiles or color as approved by engineer of size 600x600 and 0.5 mm thick with 25 mm height, made of G I sheet having galvanizing of 100 gms/ sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted etc. complete (Make: Armstrong/Hunter Douglas or equivalent)
40 | FALSE CEILING IN CORIAN SOLIDS Providing and fixing false ceiling on ground floor ceiling with circular shape and in periphery of the baffle system with aluminium pipe supports and marine ply base for taking two 6 mm double Corian Solid sheet with proper anchored, connecting, positing, polishing etc. complete | 0 | Sqm
41 | POP FALSE CEILING Providing and fixing false ceiling in Mezzanine and other areas of 12 mm thick of fibrous plaster of Paris which includes G.I. Perimeter channel ( MF6) of size 0.40 mm thick (having one flange of 20 mm and another flange of 30 mm and web of 27 mm) along with perimeter of ceiling, screw fixed to brick wall , concrete surface, partition with the help of nylon sleeves and screws at 610 mm centres. Thereafter suspending G.I. intermediate channel ( MF 7) 600 mm. C/C of size 45mm (0.9 mm thick with two flanges of 15 mm each) from the soffit at 450 mm centre with connecting angle (ie ceiling angle) of width 25mm x 10mm x 0.40mm thick fixed to soffit with G.I.cleat and steel expansion fasteners. Celling sections ( MF 5 ) of 0.55 mm thickness having knurled web of 51.5 mm and two flanges of 26 mm each with lips of 10.5 mm are then fixed to the intermediate channel with the help of connecting clip and in direction perpendicular to the intermediate channel at 450 mm centres. | 100 | Sqm
| 12.5 mm tapered edge is then screw fixed to celling section with dry wall Sqm 612.00 248.00 screws at 230 mm centres. Screw fixing is to be done mechanically with suitable attachment. The boards are to be joined and finished so as to have flush look which includes filling and finishing the tapered & square edges of the boards with jointing compound, joint paper tape and appropriate suitable primer and three coats of oil bound distemper . The item includes for light fitting, grill diffusers and cut out etc. have to be made with frame of perimeter channels of size 20mm x 30mm x 0.55mm.thick supported suitable and angle bead is to be used at steps to get straight line finish etc. complete. This also include making wooden/ ply decoration as per drawing by using CNC cutting with LED background light with glass etc. complete as directed by Engineer- in-charge | =
42 | FALSE CEILING ( 600 X 600 BOARD) Providing and fixing false ceiling of 15 mm thickness Acoustic tabular Armstrong / Everest / AMS / Aerolite or equivalent (0.6x0.6m) boards of approved make, with shapes and sizes as per drawings including powder coated G.I .wall angle of 20mmx20mm size ,G.I. grid runners of size 15mmx 38mm at 600mmcenter to centre both ways and suspended using G.I. wire 3mm wire including fixing using butter fly clips and fasteners including transporting , scaffolding, all necessary labour and machinery , finishing etc complete. (as directed by Engineer In Charge).sample to be got approved from Engineer Incharge before execution of work | 125 | Sqm
43 | ACOUSTIC WALL PANELS IN WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete. | 687.76 | Sqm
44 | WOODEN STAGE Providing and supplying wooden stage with approved quality teak wood sections and planks as per drawings and instruction of engineer incharge. (Drawing No. 07 ) | 2 | No.s
45 | STAGE BACK DROP Providing and supplying wooden wall panel with approved quality teak wood plan and sections with in vertical wall upto ceiling height including scaffolding, internal light and its cable arrangement etc. complete. | 2 | No.s
46 | 86" (INTERACTIVE TEACHING SMART BOARD) Product Code: TR3DJ TR3DJ Series Brightness: 350nits Multi Touch Point: 20 Points (Max.) Interface : HDMI (3), RGB (1), Audio In (1), RS-232C In (1), RJ45 (1), USB 3.0 Type A (3), USB 2.0 Type A (3), Audio Out / Optical Output, Touch USB (2) 4k Resolution 20 Point Multi Touch Anti-glass, Tempered Glass Screen Mirroring Minimal Air Gap Integrated Speaker and Wi-Fi Module Smooth Touch & Writing Experience Easy connection & sharing User friendly experience Make: LG 75 TR3DJ or Equivalent | 4 | No.s
47 | LECTURE HALL PROJECTOR Providing supply, installation and commissioning large-venue projector combines a laser light source and 3LCD technology for powerful, uncompromising images ideal for events staging and auditoriums with extraordinary color brightness, 3LCD projectors with brilliant images, delivering 6,000 lumens or more of color brightness and 6,000 or more lumens of white brightness1, laser light engine 3 years guarantee, connectivity to all equipments, with extra powered lenses, including, installation, cabling, remote, and screen proposed hal etc. complete (Make: Epson Pro L1100U or equivalent) | 2 | No.s
TOTAL

## FF AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR FIRST FLOOR
S/M | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 347 | SqM
2 | READY MIX CONCRETE Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centring, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete.
Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.
| All works above plinth level upto floor V level Concrete of M25 grade with minimum cement content of 330 kg /cum | 111.0851 | Cum
| Concrete of M30 grade with minimum cement content of 350 kg /cum | 26.5393 | Cum
3 | Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 36.75 | Cum
4 | Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 6.16 | Cum
5 | Cantering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 212.0385 | SqM
6 | Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 10779.6585 | Kg
7 | Providing and fixing up to floor five level precast cement concrete solid block, including hoisting and setting in position with cement mortar 1:3 (1 cement : 3 coarse sand), cost of required centring, shuttering complete. 1:1.5:3 (1 Cement: 1.5 coarse sand (zone-III) including manufactured sand derived from Recycled Concrete Aggregate (RCA) upto 25% : 3 graded stone aggregate 20 mm nominal size (Recycled Concrete Aggregate (RCA) upto 25%)). | 173.6 | Cum
8 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 150 | Cum
9 | INTERNAL PLASTER FOR ADDTIONAL ITEMS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 552.8 | SqM
10 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 258 | SqM
11 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | 889 | SqM
12 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | 266.7 | SqM
13 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 75 | SqM
| SIZE: 800 X 800 (Avg.) | 75 | SqM
| SIZE: 600 X 1200 (Avg.) | 75 | SqM
14 | MS FABRICATION WORK FOR GLAZING WORKS AND STRUCTURAL SUPPORT Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 10000 | Kg
15 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws | 23.1 | SqM
16 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm | 8.085 | Cum
17 | MAKING PAINT SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 552.8 | SqM
18 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 165.84 | SqM
19 | DUCO PAINT Providing and applying Duco paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) etc. complete. | 165.84 | SqM
20 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 165.84 | SqM
21 | TEXTURE PAINT Providing and applying texture paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 82.92 | SqM
22 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete.
| Three | 2 | No.s
| Two | 0 | No.s
23 | CABINATES/LOCKERS Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 10 | No.s
24 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 150 | SqM
25 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | SqM
26 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 25 | SqM
27 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 6 | No.s
28 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 2 | No.s
29 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 2 | No.s
30 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 2.16 | SqM
31 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 20 | SqM
32 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 250 | SqM
33 | EXTERNAL GLAZING WORK Providing and fixing external glazing in 12 mm glass in St. Gobin or equivalent with one side reflective UV protective coating in cluding all the necessary This include scaffolding, providing necessary finish, labor etc. complete | 250 | SqM
34 | FOAM SEATS IN AUDITORIUM Providing and fixing seats in auditorium with auto closing and push back mechanism of size as per drawings etc. complete
| Executive | 33 | No.s
| Regular | 590 | No.s
35 | ACOUSTIC WALL PANELS IN WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete. | 600 | SqM
36 | WOODEN STAGE Providing and supplying wooden stage with approved quality teak wood sections and planks as per drawings and instruction of engineer incharge. (Drawing No. 07 ) | 1 | No.s
37 | STAGE BACK DROP Providing and supplying wooden wall panel with approved quality teak wood plan and sections with in vertical wall upto ceiling height including scaffolding, internal light and its cable arrangement etc. complete. | 1 | No.s
38 | CEILING & WALL PANELLING : MULTI-BOX CONTINUOUS SYSTEM Providing and fixing Multi-Box Continuous metal ceiling system with 2", 4", 6" and 8' panels with ceiling suspenders, and all necessary support of same brand of available or custom colors as pe drawings or engineer incharge or approved sample etc. complete. | 150 | SqM
39 | METAL CLIP IN CEILING Providing and fixing Gl Clip in Metal Ceiling System of 600x600 mm module which includes providing and fixing 'C' wall angle of size 20x30x20 mm made of 0.5 mm thick pre painted steel along the perimeter of the room with help of nylon sleeves and wooden screws at 300 mm center to centre, suspending the main C carrier of size 10x38x10 mm made of G.I steel 0.7 mm thick from the soffit with help of soffit cleat 37x27x25x1.6 mm, rawl plugs of size 38x12 mm and C carrier suspension clip and main carrier bracket at 1000 mm c/c. Inverted triangle shaped Spring Tee having height of 24 mm and width of 34 mm made of Gl steel 0.45 mm thick is then fixed to the main C carrier and in direction perpendicular to it at 600 mm centers with help of suspension brackets. Wherever the main C carrier and spring T have to join, C carrier and spring T connectors have to be used. All sections to be galvanized @ 120 gms/sqm (both side inclusive), fixing with clip in tiles into spring T with : |  | SqM
40 | GI Metal Ceiling Clip in plain Bevelled edge global white color tiles or color as approved by engineer of size 600x600 and 0.5 mm thick with 25 mm height, made of G I sheet having galvanizing of 100 gms/ sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted etc. complete (Make: Armstrong/Hunter Douglas or equivalent) | 80 | SqM
41 | FALSE CEILING IN CORIAN SOLIDS Providing and fixing false ceiling on ground floor ceiling with circular shape and in periphery of the baffle system with aluminium pipe supports and marine ply base for taking two 6 mm double Corian Solid sheet with proper anchored, connecting, positing, polishing etc. complete | 0 | SqM
42 | POP FALSE CEILING Providing and fixing false ceiling in Mezzanine and other areas of 12 mm thick of fibrous plaster of Paris which includes G.I. Perimeter channel ( MF6) of size 0.40 mm thick (having one flange of 20 mm and another flange of 30 mm and web of 27 mm) along with perimeter of ceiling, screw fixed to brick wall , concrete surface, partition with the help of nylon sleeves and screws at 610 mm centres. Thereafter suspending G.I. intermediate channel ( MF 7) 600 mm. C/C of size 45mm (0.9 mm thick with two flanges of 15 mm each) from the soffit at 450 mm centre with connecting angle (ie ceiling angle) of width 25mm x 10mm x 0.40mm thick fixed to soffit with G.I.cleat and steel expansion fasteners. Celling sections ( MF 5 ) of 0.55 mm thickness having knurled web of 51.5 mm and two flanges of 26 mm each with lips of 10.5 mm are then fixed to the intermediate channel with the help of connecting clip and in direction perpendicular to the intermediate channel at 450 mm centres.
| 12.5 mm tapered edge is then screw fixed to celling section with dry wall Sqm 612.00 248.00 screws at 230 mm centres. Screw fixing is to be done mechanically with suitable attachment. The boards are to be joined and finished so as to have flush look which includes filling and finishing the tapered & square edges of the boards with jointing compound, joint paper tape and appropriate suitable primer and three coats of oil bound distemper . The item includes for light fitting, grill diffusers and cut out etc. have to be made with frame of perimeter channels of size 20mm x 30mm x 0.55mm.thick supported suitable and angle bead is to be used at steps to get straight line finish etc. complete. This also include making wooden/ ply decoration as per drawing by using CNC cutting with LED background light with glass etc. complete as directed by Engineer- in-charge | 110.4 | SqM
43 | FALSE CEILING ( 600 X 600 BOARD) Providing and fixing false ceiling of 15 mm thickness Acoustic tabular Armstrong / Everest / AMS / Aerolite or equivalent (0.6x0.6m) boards of approved make, with shapes and sizes as per drawings including powder coated G.I .wall angle of 20mmx20mm size ,G.I. grid runners of size 15mmx 38mm at 600mmcenter to centre both ways and suspended using G.I. wire 3mm wire including fixing using butter fly clips and fasteners including transporting , scaffolding, all necessary labour and machinery , finishing etc complete. (as directed by Engineer In Charge).sample to be got approved from Engineer Incharge before execution of work | 100 | SqM
TOTAL

## SF AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR SECOND FLOOR
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 694 | SqM
2 | READY MIX COCNRETE Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centring, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete.
Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.
| All works above plinth level upto floor V level Concrete of M25 grade with minimum cement content of 330 kg /cum | 111.0851 | CuM
| Concrete of M30 grade with minimum cement content of 350 kg /cum | 24.6249 | CuM
3 | RCC SLAB Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 135.2 | CuM
4 | RCC WAIST SLAB Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 6.16 | CuM
5 | Cantering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 125.5955 | SqM
6 | HYSD REINFROCEMENT Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 13849.2673 | Kg
7 | Providing and fixing up to floor five level precast cement concrete solid block, including hoisting and setting in position with cement mortar 1:3 (1 cement : 3 coarse sand), cost of required centring, shuttering complete. 1:1.5:3 (1 Cement: 1.5 coarse sand (zone-III) including manufactured sand derived from Recycled Concrete Aggregate (RCA) upto 25% : 3 graded stone aggregate 20 mm nominal size (Recycled Concrete Aggregate (RCA) upto 25%)). | 772.29 | CuM
8 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 150 | CuM
9 | INTERNAL PLASTER FOR ADDTIONAL ITEMS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 220.805 | SqM
10 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 478 | SqM
11 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | 889 | SqM
12 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | 266.7 | SqM
13 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 75 | SqM
| SIZE: 800 X 800 (Avg.) | 75 | SqM
| SIZE: 600 X 1200 (Avg.) | 75 | SqM
14 | MS FABRICATION WORK FOR GLAZING WORKS AND STRUCTURAL SUPPORT Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 10000 | Kg
15 | DOORS (WITHOUT FRAMES) Providing and fixing country teak wood single leaf, 2nd class partly panelled door as per drawings including iron oxidised fixtures and fastenings and finishing the wood work with one coat of primer etc.(excluding door frame) complete. | 23.1 | SqM
16 | DOOR FRAMES Providing and fixing first quality wood door frame of sizes 125x 62mm , 75 x 50 mm or any other size with 12 mm rebate for door shutter including superior grade melamine polishing etc. The base & side touching the floor/partition to be applied with ant termite treatment. The rate shall be inclusive of fixing necessary hardware for fixing the frame to partition etc. complete | 9.24 | CuM
17 | MAKING PAINT SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 220.805 | SqM
18 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 66.2415 | SqM
19 | DUCO PAINT Providing and applying Duco paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) etc. complete. | 66.2415 | SqM
20 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 66.2415 | SqM
21 | TEXTURE PAINT Providing and applying texture paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 33.1208 | SqM
22 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete.
| Three | 2 | No.s
23 | CABINATES/LOCKERS Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). | 10 | No.s
24 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 150 | SqM
25 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | SqM
26 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 4 | SqM
27 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 6 | No.s
28 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 2 | No.s
29 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 2 | No.s
30 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 2.16 | SqM
31 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 20 | SqM
32 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 75 | SqM
33 | EXTERNAL GLAZING WORK Providing and fixing external glazing in 12 mm glass in St. Gobin or equivalent with one side reflective UV protective coating in cluding all the necessary This include scaffolding, providing necessary finish, labor etc. complete | 353.7 | SqM
34 | CEILING & WALL PANELLING : MULTI-BOX CONTINUOUS SYSTEM Providing and fixing Multi-Box Continuous metal ceiling system with 2", 4", 6" and 8' panels with ceiling suspenders, and all necessary support of same brand of available or custom colors as pe drawings or engineer incharge or approved sample etc. complete. | 95 | SqM
35 | METAL CLIP IN CEILING Providing and fixing Gl Clip in Metal Ceiling System of 600x600 mm module which includes providing and fixing 'C' wall angle of size 20x30x20 mm made of 0.5 mm thick pre painted steel along the perimeter of the room with help of nylon sleeves and wooden screws at 300 mm center to centre, suspending the main C carrier of size 10x38x10 mm made of G.I steel 0.7 mm thick from the soffit with help of soffit cleat 37x27x25x1.6 mm, rawl plugs of size 38x12 mm and C carrier suspension clip and main carrier bracket at 1000 mm c/c. Inverted triangle shaped Spring Tee having height of 24 mm and width of 34 mm made of Gl steel 0.45 mm thick is then fixed to the main C carrier and in direction perpendicular to it at 600 mm centers with help of suspension brackets. Wherever the main C carrier and spring T have to join, C carrier and spring T connectors have to be used. All sections to be galvanized @ 120 gms/sqm (both side inclusive), fixing with clip in tiles into spring T with : | 174 | SqM
GI Metal Ceiling Clip in plain Bevelled edge global white color tiles or color as approved by engineer of size 600x600 and 0.5 mm thick with 25 mm height, made of G I sheet having galvanizing of 100 gms/ sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted etc. complete (Make: Armstrong/Hunter Douglas or equivalent)
36 | FALSE CEILING IN CORIAN SOLIDS Providing and fixing false ceiling on ground floor ceiling with circular shape and in periphery of the baffle system with aluminium pipe supports and marine ply base for taking two 6 mm double Corian Solid sheet with proper anchored, connecting, positing, polishing etc. complete | 0 | SqM
37 | POP FALSE CEILING Providing and fixing false ceiling in Mezzanine and other areas of 12 mm thick of fibrous plaster of Paris which includes G.I. Perimeter channel ( MF6) of size 0.40 mm thick (having one flange of 20 mm and another flange of 30 mm and web of 27 mm) along with perimeter of ceiling, screw fixed to brick wall , concrete surface, partition with the help of nylon sleeves and screws at 610 mm centres. Thereafter suspending G.I. intermediate channel ( MF 7) 600 mm. C/C of size 45mm (0.9 mm thick with two flanges of 15 mm each) from the soffit at 450 mm centre with connecting angle (ie ceiling angle) of width 25mm x 10mm x 0.40mm thick fixed to soffit with G.I.cleat and steel expansion fasteners. Celling sections ( MF 5 ) of 0.55 mm thickness having knurled web of 51.5 mm and two flanges of 26 mm each with lips of 10.5 mm are then fixed to the intermediate channel with the help of connecting clip and in direction perpendicular to the intermediate channel at 450 mm centres.
| 12.5 mm tapered edge is then screw fixed to celling section with dry wall Sqm 612.00 248.00 screws at 230 mm centres. Screw fixing is to be done mechanically with suitable attachment. The boards are to be joined and finished so as to have flush look which includes filling and finishing the tapered & square edges of the boards with jointing compound, joint paper tape and appropriate suitable primer and three coats of oil bound distemper . The item includes for light fitting, grill diffusers and cut out etc. have to be made with frame of perimeter channels of size 20mm x 30mm x 0.55mm.thick supported suitable and angle bead is to be used at steps to get straight line finish etc. complete. This also include making wooden/ ply decoration as per drawing by using CNC cutting with LED background light with glass etc. complete as directed by Engineer- in-charge | 100 | SqM
38 | FALSE CEILING ( 600 X 600 BOARD) Providing and fixing false ceiling of 15 mm thickness Acoustic tabular Armstrong / Everest / AMS / Aerolite or equivalent (0.6x0.6m) boards of approved make, with shapes and sizes as per drawings including powder coated G.I .wall angle of 20mmx20mm size ,G.I. grid runners of size 15mmx 38mm at 600mmcenter to centre both ways and suspended using G.I. wire 3mm wire including fixing using butter fly clips and fasteners including transporting , scaffolding, all necessary labour and machinery , finishing etc complete. (as directed by Engineer In Charge).sample to be got approved from Engineer Incharge before execution of work | 125 | SqM
39 | AUDITORIUM CEILING: CURVE TORSION SPRING METAL CEILING SYSTEM Providing and fixing curved torsion spring metal ceiling system 42" and 96" long in custom color as per drawing or engineer incharge or as per sample approved by client with laminated (film) wood finish or as suggested by engineer with suspenders etc. complete. It also include making POP ceiling for provision of AC and lights between the panels. (Make: Hunter Douglas/Armstrong or Equivalent) | 421.2 | SqM
40 | CUVERED BAFFLED CEILING IN LOBBY Providing and fixing soundcspe curved metal ceiling system in any texture (including wooden), color, design and modification any as approved by the engineer including complete system of the suspender as per the manufacturer specification etc. complete (Make: Hunter Douglas/Armstrong or equivalent) | 350 | SqM
41 | 86" (INTERACTIVE TEACHING SMART BOARD) Product Code: TR3DJ TR3DJ Series Brightness: 350nits Multi Touch Point: 20 Points (Max.) Interface : HDMI (3), RGB (1), Audio In (1), RS-232C In (1), RJ45 (1), USB 3.0 Type A (3), USB 2.0 Type A (3), Audio Out / Optical Output, Touch USB (2) 4k Resolution 20 Point Multi Touch Anti-glass, Tempered Glass Screen Mirroring Minimal Air Gap Integrated Speaker and Wi-Fi Module Smooth Touch & Writing Experience Easy connection & sharing User friendly experience Make: LG 75 TR3DJ or Equivalent | 1 | SqM
42 | AUDITOIRUM PROJECTOR Providing supply, installation and commissioning large-venue projector combines a laser light source and 3LCD technology for powerful, uncompromising images ideal for events staging and auditoriums with extraordinary color brightness, 3LCD projectors with brilliant images, delivering 6,000 lumens or more of color brightness and 6,000 or more lumens of white brightness1, laser light engine 3 years guarantee, connectivity to all equipments, with extra powered lenses, including, installation, cabling, remote, and screen proposed hal etc. complete (Make: Epson Pro L1100U or equivalent) | 1 | No.s
43 | CONFERENCE TABLE Providing and fixing conference table with base made up of solid teak wood frame fitted with 18 mm water proof marine ply. Ply will have teak veneer 3.5 mm thick of century or equivalent. This include polishing, base coat and \finishing table top. Table top will have electric points in SS 304 Matt finish doors as per drawings, All the edges will be smooth. This item also include electrical fitting of push type for conference table including cable holes in cables. Also making concealed connection through floor with sufficient points for laptop etc. complete. |  | No.s
44 | CONFERENCE HALL CHAIRS Providing and supplying conference hall rolling and revolving chairs of approved make and model etc. complete. | 14 | No.s
45 | MODULAR KITCHEN PLATFORM FOR PANTRY Providing and fixing Modular kitchen as per drawings with polished Stainless Steel platform with large size Stainless Steel wash basin with S trap and cleaning Jali. Modular kitchen will be made form 18 mm thick marine ply with glazed finished laminates of white and black colors with Hettich fittings of auto swing/close type. Internal wet and dry arrangement shall be made with use of Stainless Steel trays with all system for crockery, utensils, spoons, knifes etc. complete. Framing of the modular kitchen shall be in MS pipes with pure polyester coating from inside and outside. Powered coating shall be provided above pure polyester coat of approved quality, color, micron etc. complete. Kota stone base shall be provided to the SS platform. Proper slope for drain in Platform and floor shall be provided with Nahani trap. Electrical points at suitable locations shall be provided at suitable locations. | 1 | No.s
Additional glass cookery cabinet on wall above platform of approved quality and as per design shall be provided. electronic exhaust chimney of approved make shall be provided by the contractor. Any additional requirements shall be clarified before quoting for this item.
46 | CABINATE IN PANTRY Providing and fixing 3.2 m (l) x 0.45 (w) x 3.0 (h) cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 1 | No.s
Total

## TF AUDI
NAME OF WORKS: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR TERRACE FLOOR
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 1367 | SqM
2 | BRICK WORK Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 45 | CuM
3 | WATER PROOF CEMENT PAINT Providing and applying two coats of waterproof cement paint of an approved make and colour as per manufacturers specifications to smooth sand faced or other surfaces, upto 10m height from ground level and at all locations as directed including preparing surfaces for painting by any approved means, watering, scaffolding, cleaning and curing etc. complete as directed by Engineer-in-charge. | 150 | SqM
4 | UPVC PIPES AND BENDS Providing and fixing UV resistant self fit UPVC pipes of approved make for Rainwater down takes confirming to IS 13592:1992 Type A suitable for 4kg/sqcm pressure for following pipe diameters including rain water receiving recess with pvc plug bend necessary fittings such as offsets shoes, fixing the pipes on wall with clips filling the joints with solvent/cement and necessary scaffolding etc. complete as directed by Engineer In Charge. 150mm dia | 150 | Rmt
5 | WATER PROOFING TO TERRACE Providing water proofing treatment of Old Terraces by removing existing treatment. Sealing of cracks by non shrink cracks fill compound by applying first coat of polymer modified semi-viscous paste prepared by mixing polymer of approved make (such as Aquatek conchem/ Master Seal 550/brush bond / RoffSupercrete/ Webercrete/ Monobond / Perma shield / Hypercrate / Master Crete M 81/ MC-Bauchemie) and Cement in 1:2proportion ( 1 litre polymer : 2 Kg Cement) or Rohnex water proofing system in two coats(1kg powder,700 ml water and polymer jelly for first coat & 1 kg powder,500 ml water & polymer jelly for second coat) to a neatly cleaned and dust free concrete surface and upto 300 mm over parapet wall prepared by removing loose and deposited material with brush and water, laying glass fibre mesh of 10 x 10 specification of approved make over tacky surface of first coat of polymer followed by second coat in transverse direction, laying mechanical protective cover to polymer coating treatment with brick bat coba with burnt broken brick bats laid in C.M. 1:5 admixed with approved water proofing compound, filling up to half depth of brick bats, curing this layer for 3 days, | 1367 | Sq.M
applying cement slurry over this layer joints of brick bats with C.M. 1:3 admixed making the Sq.m. 1102.00 219.00 junctions at the parapet rounded and tapered top for required height, with drip mould at the junction of plaster and parapet and curing and covering 7 years Guarantee against leak proofness on court including ponding test etc. complete (Make: Dr. Fixit Roofseal or equivalent)
6 | GROUTING TO VARIOUS PARTS Providing Grouting by specially prepared grout of Weber Crete /Roff Supercrete /Polyalk P/Monobond /Perma shield/Hypercrate or equivalent with cement in proportion 1:3.5 (1 part chemical & 3.5 part cement by weight) along with 50 ml super plasticizer Roff Plast 320/sun polycrete NCT/Perma Plast/Supercon 100 or non shrinking, non cracking antiwash high strength polymer cement grout P C grout available in bags or equivalent with proper water for injectable consistency and applying it in the body of structure like slab, beam, column, pillars, deckslab, retaining wall, basement, underground and elevated water storage reservoir concrete and brick wall, crack portion of structure etc. by injectng method, to achieve its original strength including drilling of suitable diameter drills holes at 2 to 4 Nos. per sqm. using caps and nozzle grouting machinery necessary, scaffolding, finishing and covering gurantee of 10 years and necessary testing etc. complete. | 250 | Kg
7 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 250 | SqM
8 | STEEL WORK FOR ROOFING Providing, detailing, composite fabricating members like Trusses, Girders, girders, bracings, supports, purlins, runners, and similar structural steel members fabricated using M.S. hollow tubular steel sections (circular & rectangular pipes), including transportation of the same to site, erection of structural steel members for all heights & at all levels, provision of necessary erection bolts, fixing bolts, nuts, washers, cleats, stiffeners, gussets, base plate, and all necessary operations like preheating as per specifications, straightening, bending, cutting, drilling, grinding, machining if specified, welding, grinding, removing the welding burr and preparing surface for painting with wire brush cleaning and applying two coats of epoxy red oxide zinc phosphate primer of 30 microns each and two coats of Epoxy Corrosion Resistant Enamel paint of 30 microns after fabrication including touching up with spray painting after erection etc complete as directed by Engineer In Charge. | 15000 | Kg
| Providing and fixing box type gutter of width 350 mm and depth 250 mm clear inside, made of 22 gauge G.I.sheets with socket type opening on top to receive ferrules from longitudinal truss gutters and ferrules at end, with all the fixtures and fastenings and three coats of synthetic enamel paint, gutters to be supported on M.S. flat hangers 750 MM C/C which are fixed on top as directed and laid to proper slope, as specified including making necessary connections with rain water pipes etc complete and as directed. (Rate includes cost of hangers, the fixing charges, 3 coats of synthetic enamel paint, and welding if required). | 150
9 | ROOF SHEETS Providing and fixing single skin trapezoidal profiled sheeting 930 - 1020mm cover width 28-32 mm crests depth at 186-250 c/c ( above 195 mm c/c crest distance there will be minimum 2 ribs at the centre for stiffening). The feed material shall be manufactured from AZ 150 (min. 150 gms/sq.mt total on both sides) Zincalume / Galvalume sheets of minimum yield strength of 550 MPa, 0.45 mm BMT, ( 0.5 mm TCT excluding paint coating thickness), metallic hot dip coated with Al-Zn alloy (55% Aluminium, 43.5% Zinc, 1.5% Si ) as per AS 1397 / IS15961 & painted with Super Durable Polyester Colorbond steel XRW or equivalent quality paint system of approved color, suitable for exterior application conforming to AS/NZS 2728:2007 type-4 / IS15965:class3 of approved make. The sheet shall have a total coating thickness of 35 microns, super durable polyester paint system of 20 microns on exposed surface and 5 micron reverse polyester coat on back surface over 5 micron primer coat on both surfaces. The paint system shall have stable inorganic pigments for color durability. The product will be fastened using no.12-14x55 mm
| (or as per design requirement ), mechanically coated with 25 micron Zn-Sn alloy or hot dipped zinc coated with min 40 micron hex self-drilling fasteners with EPDM washer of approved make confirms to AS3566:2002 class 3. The fastener shall be fixed on every crest of sheets for connecting with purlins. The contractor is to submit design and workshop drawings and take approval on the sheet profile, design and detail before installation of the sheets from the concerned authorities.(The measurement shall be based on per unit of finished/covered surface area.) Colour Coated Galvalume/zincalume Flashings and Cappings 600mm wide | 1388 | SqM
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## SANI AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR SANITATION WORK FOR ALL FLOOR
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | WHITE COLOR WATER CLOSET Providing & Fixing star white color vitreous China wall mounted water closet with heavy duty soft close seat cover & concealed dual tank. Complete with all accessories like pipes, cistern etc. including cutting & making good wall & floor wherever required. (Model PERRYWARE PETIT S OR Equivalent Standards Dimension: 380*360*545 or more) | 33 | No
2 | WHITE COLOR WASH BASIN OVAL SHAPE Providing & Fixing star white color vitreous China wash basin Oval shape, 32mm dia C.P waste, 32mm Dia C.P wall flange & rubber adopter for waste connection complete, including cutting & making good the walls wherever required. (Model - Perryware Cascase NXT BC Basin or Equivalent Dimension: 555 x 450 x 205 or more) Note: Contractor shall approve the make and design from Engineer Incharge. | 15 | No
3 | WHITE COLOR URINAL Providing & Fixing star white color vitreous China urinal with inbuilt auto flush system with s.s. bracket, pipe to wall with C.P flange compete including cutting & making good the walls & floors wherever required. Model Perryware New Magnum Standard Urinal, or Equivalent, Dimension: 380*400*590 or more) Note: Contractor shall approve the make and design from Engineer Incharge. | 9 | No
4 | STAINLESS STEEL SINK Providing & Fixing in position best stainless steel sinks with 40mm C.P. brass waste chrome plated & s.s. waste pipe. complete in all respect including cutting & making good the walls & floors. in canteen. Jaguar/Sunfold/Equivalent 24"X20"X8" 1.0mm thick mat finish. Note: Contractor shall approve the make and design from Engineer Incharge Embassy | 2 | No
5 | WALL MOUNTED TAP Providing & Fixing chrome plated wall mounted taps over wash basin complete in all respect including cutting & making good the walls wherever required (Make: As approved by the Engineer Incharge) | 21 | No
6 | STOP TAP FOR WATER CLOSET Providing & Fixing 15mm C.P brass bib tap for water closet with C.P brass threaded flange complete, including cutting & making good the walls wherever required. Model - : Contractor shall approve the make and model form Engineer Incharge | 33 | No
7 | ANGLE VALVE FOR WATER CLOSET Providing & Fixing 15mm C.P. brass angle valve with C.P copper connecting pipe 375mm long & nuts, washer & C.P. brass flange complete, including cutting & making good the wall wherever required. JAQUAR CONTINENTAL 053 KN for water closet cistern & basins. or Equivalent in Kohler/TOTO/American Standards | 33 | No
8 | STOP COCK FOR URINAL BEFORE SENSOR Providing & Fixing concealed stop cocks for cold water supply. Note: Contractor shall approve the make and design from Engineer Incharge Embassy | 5 | No
9 | BRASS MIXING FITTING FOR SINK Providing & Fixing 15mm C.P. brass mixing fitting for sink with swinging spout complete, including cutting & making good the walls wherever required. Wall mixer with swivel spout. Note: Contractor shall approve the make and design from Engineer Incharge Embassy | 2 | No
10 | AUTOMATIC SOAP DISPENSER Providing & Fixing ABS body automatic liquid soap dispenser for all was basins with liquid soaps. Note: Contractor shall approve the make and model from Engineer Incharge Embassy) | 17 | No
11 | CROMIUM PLATED TOWEL ROD 16 MM DIA Providing and fixing chromium plated towel rod 16 mm dia. and 75 cm. in length including all accessories, fitting, cleaning, etc. complete. | 14 | No
12 | PVC NAHANI TRAP Providing and fixing 150 cm Rigid PVC Nahani Trap including PVC grating, bend, connecting piece of P.V.C.pipe of required diameter, pipe up to the outside face of the wall, making good the holes and repairs, testing, including cover etc. complete. | 40 | No
13 | MIRROR IN TOILET Providing and fixing 2000 mm x 900 mm size superior type mirror with 16 mm dia including chromium plated towel rod etc. complete. Note: Contractor shall approve a sample from architect/engineer incharge | 10 | No
14 | PIPE FOR DRAINAGE Providing and fixing in position Heavy type alkathene pipe for drainage connections including cutting, boring holes in wood work or masonry if necessary, making connections of pipe to sink and giving test for no leakages, making good the damaged surface etc. complete. As directed by Engineer in-charge
| 25 MM Dia | 3000 | Rmt
| 40 MM Dia | 2500 | Rmt
15 | PIPE FOR RAINWATER DRAINAGE Providing and fixing in position Heavy type alkathene pipe for drainage connections including cutting, boring holes in wood work or masonry if necessary, making connections of pipe to sink and giving test for no leakages, making good the damaged surface etc. complete. As directed by Engineer in-charge Embassy.
| 250 MM Dia | 750 | Rmt
16 | UPVC WASTE PIPE Providing and fixing UPVC waste pipes for Wash Basin / Urinals including all fittings, making chases in wall / floor and reinstating the surface. etc. complete. As directed by Engineer in-charge Embassy.
| 50 mm Dia | 750 | Rmt
| 40 MM Dia | 1500 | Rmt
17 | PVC PIPE Providing, cutting, erecting, jointing, clamping, fixing including making clamping, fixing including making opening in walls, floors, S.W.R., P.V.C. pipe and fittings, such bends, elbows single junction, double junctions, cowls with PVC / G.I. brackets etc. including jointing with solvent cement/rubber ring, making necessary holes in masonry / concrete, all installation as workmanship like manner and as per manufacturer's instructions, testing, commissioning the lines, attending to leakage if any making it to good leakage if any making it to good condition. Following diameters of S.W.R.PVC pipe and fittings of approved make conforming to IS 13592-1992. All as directed.
| 110 mm. dia. PVC pipe for soil stack | 350 | Rmt
| 75 mm. dia. PVC pipe for waste wear pipe | 250 | Rmt
| 50 mm. dia. PVC pipe for anti-symphonic pipe | 75 | Rmt
18 | RECTANGULER TISSUE PAPER HOLDER FOR LADIES AND GENT TOILET Providing and fixing rectangular tissue paper holder in ladies and gents toilet for holding hand wash tissue papers, with additional storage facilities etc. complete (Model: As approved by Engineer Incharge) | 33 | No
19 | TOILET TISSUE PAPER HOLDER Providing and fixing toilet tissue paper holder in ladies and gents toilet for holding hand wash tissue papers, with additional storage facilities etc. complete (Model: As approved by Engineer Incharge) | 30 | No
20 | WATER TANK Providing and fixing PVC tank of appropriate capacity in basement, roof and other places etc. complete | 15000 | Ltrs
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## ELE AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR ELECTRICAL WORK FOR ALL FLOORS
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | POINT WIRING FOR INDEPENDENT PLUG Providing, fixing and testing point wiring for independent plug in 20 mm rigid PVC conduit with 1.5 sqm FRLS grade Copper wire with modular switch and concealed wiring with necessary joints, and required accessories complete. As directed by Engineer in-charge | 390 | No.s
2 | LIGHT POINT WITH SINGLE MODULER SWITCH Providing, fixing and testing light point with single modular switch with concealed cables and modular plate etc. complete. | 441 | No.s
3 | POINT WIRING FOR WALL MOUNTED FANS Providing, fixing and testing point wiring for wall mounted fans in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade Copper wire with flush type switch and required accessories etc. complete. | 70 | No.s
4 | CEILING FANS Providing, supplying and fixing ceiling fans of with regulator and all other accessories, etc. complete (Make: Bajaj or equivalent) | 28 | No.s
5 | CONCEALED SQUARE LED LIGHT FIXTURE Supply, Installation, testing & commissioning of the 2x36 watt, 2x2” size concealed light fixture as per drawings complete with LED system etc. (Make: Philips: Green Square 39W 2x2 LED Light or equivalent) with switches etc. | 107 | No.s
6 | LED BATTEN LIGHTS Supply, Installation, testing & commissioning of the 36 watt or above, concealed LED circular light fixture in console room complete with copper choke, starter, LED etc. (Make PHILIPS Mirolta Pro r16 36 Watts LED Batten - High Power High Performance Tube Light - Cool Day Light or equivalent) | 32 | No.s
7 | CEILING CIRCULER LIGHT PANEL Supply, installation, testing & commissioning of white color ceiling fixture of material metal and glass with 15 watt or above LED light including, started, LED system, switches etc, complete (Make: Philips myLiving canvas white model no. 77050/31/16 or equivalent) | 223 | No.s
8 | STEPS AND RAMP LIGHTING Supply, Installation, testing & commissioning for steps in auditorium, steps, below seats and ramp lighting of the watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania: wall 5 STE DIR 4W LED WHT LLB with switches etc. | 300 | No.s
9 | PENDENT LIGHT IN LOBBY Providing, installation, testing & commissioning of 6-1/2’’ Pendalyte with Satined Aluminium Reflector, with suspended, lamp holder, LED/CFL lamp of 32 watt and above etc. complete (Make: Philips Pendalyte with Satined Aluminium Reflector or equivalent) | 30 | No.s
10 | HANGING LIGHT FIXTURES FIXTURE Supply, Installation, testing & commissioning hanging light fixtures in lotus shape made from brass of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested
| Large | 25 | No.s
| Small | 15 | No.s
11 | WALL LED LIGHT Providing, supplying, installation as commissioning, regular 26 watt and above light fixtures with light holder of approved quality including concealed cabling, modular switch, texted as approved by engineer, with wiring, scaffolding, etc. complete (PHILIPS 26-watt LED Bulb ¦Ace Bright High Wattage LED Bulb Base: B22 Light Bulb for Home ¦ Crystal White or equivalent) | 35 | No.s
12 | WALL MOUNTED FIXTURE Supply, Installation, testing & commissioning for curved wall in console room of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested | 20 | No.s
13 | LED TUBE ON TERRACE Supply, installation, testing and commission of LED tube25 watt or above of material glass and plastic including bulb, clips, LED system, civil work etc complete(Make: Philips Linea 26-Watt LED Tube (White) or equivalent) | 16 | No.s
14 | LED STRIP LIGHTS Supply, installation, testing and commissioning of LED strip lights 8 watt above per metre of required color or hue including, adaptor, controller, male-female clips, cable, switches etc. complete in ceiling, tables, with scaffolding, glass etc. complete. (Make: Philips 800284 Hue Light strip Plus, 2Nd Generation or equivalent) | 50 | No.s
15 | EXTERIOR LED LIGHTS FOR BUILDING Supply, Installation, testing & commissioning for lights in exterior in elevation of LED or compliance concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. Contractor shall assign specialised company for design and installation of external lighting with previous experience in similar field. Contractor and subcontractor shall approve the design for external lighting from architect or engineer any suggestions shall be incorporated with all necessary requirement etc. complete This item include AMC for three years.. | 1 | No.s
16 | POINT WIRING FOR LAN POINTS Point wiring for LAN points will be carried out with CAT 6, LAN Cable, in surface/ recessed existing PVC conduits, inclusive of p/f of G.I/ PVC box & modular plate RJ 45 AT&T LAN socket. Work includes cutting & repair of chase to original finish. (Make of cable: Polycab or equivalent) | 52 | No.s
17 | CIRCUIT WIRING Supply and wiring wall / floor etc. / recessed / surface as per colour code with the following size PVC Insulated copper wire along with given earth wire for phase neutral and earth conductor with standard colour coding, through ISI marked rigid PVC conduit of given size with all accessories. The rate includes the cost of complete wiring from switch box to switch box etc. complete (Make of wire: Polycab or equivalent)
a. | 2 x 1.0 Sqmm PVC Copper wire in 20 mm dia conduit for Emergency Stop Box Connection | 1800 | Rmt
b. | 3 x 1.5 Sqmm PVC Copper wire with in 20 mm dia conduit (The rate includes the cost of complete wiring between individual switch boards) | 1800 | Rmt
c. | 3 x 2.5 Sqmm PVC Copper wire with in 20 mm dia conduit (for lighting main circuit, 15A plug points & UPS point wiring & 1T AC) | 2500 | Rmt
d. | 5 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 3-Ph circuits like 3-Ph AC / UPS) | 2000 | Rmt
e. | 3 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 1.5/2Tonne AC and UPS I/P & O/P upto UPS O/P DB and for Sign Boards if there are multiple Name boards) | 950 | Rmt
18 | AC/HEATER METAL BOX Supplying and fixing for AC/Heater metal box of GI box with modular plate and cover in front on surface or in recess , including providing and fixing of 3 No's 3 pin 5/6 amps modular socket outlet and 15/16 amps. Modular switch, connections, painting etc. as required | 57 | No.s
19 | TWO WAY CONNECTIONS Point wiring for two way connects for switching lights in corridor, toilet, landscape, steps in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade copper wire with flush type switch and required accessories. | 50 | No.s
20 | UTP NETWORK CABLE CAT 6 Supplying & installing UTP networking Cat-6+ cable suitable for LAN / WAN Computer networking. | 52 | No.s
21 | M. S. CABLE TRAY Fabrication and installing required sizes of perforated M.S. cable trays including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with M.S. suspenders and including painting with powder coating etc. as required. | 1 | No.s
22 | DISTRUBUTION BOARD Distribution board of approved make as per design requirements of Legrand or equivalent make with MCB cables, separation for computers, lights etc. complete | 40 | No.s
23 | PVC CABLE Supply and erecting PVC armoured cable 2 core 2.5 sq. mm stranded/solid copper conductors continuous 5.48 sq. mm (12 swg) GI earth wire complete erecting with glands & lugs on wall in trenches complete (Measurement to be as per site condition and location of Mains) (Make: Polycab or equivalent) | 2500 | Rmt
24 | SUPPLY 16" EXHAUST FAN Supply of 16" exhaust fan of PVC of high speed with installation, testing including aluminium or wooden framing etc. complete. (Make Godrej/Philips or equivalent) Note: Contractor shall approve the make and model from Engineer in-charge of Embassy) | 21 | No.s
25 | BELL POINTS Providing and fixing bell points with concealed conduits with cable, bell of approved make, modular switches, etc. complete | 15 | No.s
26 | TELEPHONE POINTS Providing and fixing telephone points with modular plate, cable, switch with concealed cabling etc. complete | 20 | No.s
27 | EARTHLING WITH G.I. EARTH PIPE Earthling with G.I. earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but without charcoal or coke and salt) as required. | 25 | No.s
28 | MUSIC CUM PA SYSTEM OF PHILIPS MAKE Providing and fixing music systems of Philips make with speakers, CD, USB, Radio etc. complete as approved by engineer incharge with stereo speakers in appropriate locations, including stereo head phones etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. Design & product detail to be submitted with tender. | 4 | No.s
29 | MODULAR KITCHEN HOT PLATE Providing and fixing modular kitchen hot plate with 4 no. of coils of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. | 4 | No.s
30 | MODULAR KITCHEN GRILL AND OVEN Providing and fixing modular kitchen grill and oven of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. | 4 | No.s
31 | MODULAR KITCHEN FRIDGE Providing and fixing modular kitchen fridge of approved size and capacity Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer incharge Embassy. | 1 | No.s
32 | WATER HEATER Supplying, installation, and testing Smith-Jaguar water heater with all accessories in Male and Female toilets complete. (Make: Jaguar CEWHR-DIGITAL Digital with remote & dual heating elements 35 19.00 395X760 1 KW/ 1.5 KW/ 2.5 KW) | 8 | No.s
33 | ELECTRICAL PANEL Suppling, installation, commissioning of main electrical panel in basement for all electrical equipments with all necessary requirements as approved by architect or engineer etc. complete. | 4 | No.s
34 | LANDSCAPE LIGHTS Providing and fixing landscape lights with fixture of approved make and models as per the design with weather protection of Philips or equivalent make with connections, installation etc. complete | 40 | No.s
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## CCTV AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ FOR CCTV SYSTEM
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DOME CAMERAS Supply Installation ,Testing & Commissioning for cctv Camera, Specification: High Resolution Digital Image Sensor HIKVISION 5 MP Indoor Dome CCTV Camera with inbuilt Audio Mic DS-2CE76H0T-ITPFS + USEWELL BNC/DC, White Wired, 1080P Image Sensor (Make: HIKVISION or Equivalent) | 44 | No.s
2 | BULLET CAMERAS Supply Installation Testing & Commissioning for cctv camera, Specification: HIKVISION 2MP Eco HD 1080P Night Vision Bullet Outdoor Wired CCTV Camera for 2MP & Above DVRs, White (Model: Hikvision or Equivalent) | 4 | No.s
3 | PTZ CAMERAS Supply installation and commissioning of CCTV camera etc. complete ( Make: HIKVISION 2-inch 4 MP Color Mini PT Dome Network Camera DS-2DE2C400SCG-E Compatible with JK Vision BNCor Equivalent) | 1 | No.s
4 | CONNECTOR FOR CCTV CAMERAS Connector for cctv camera, adaptor, | 50 | No.s
5 | NETWORK VIDEO RECORDER Supply, installation and commissioning of NVR:64 Channel 4K NVR, Plug And Play Black, Up to 8 SATA interfaces Third-party network cameras supported Up to 12 Megapixels resolution recording Support various VCA detection alarm and VCA search Support HDD hot swap with RAID0,1,5,6,10 storage scheme configurable etc. complete (Make: Hikvision DS-9664NI-I8 or equivalent) | 1 | No.s
6 | CAT 6 CABLE Cat 6 Cable including making hole, taking though ceiling though pipe, concealing, scaffolding etc. complete | 1000 | Rmt
7 | JOYSTICKS FOR CCTV CAMERAS CCTV LCD Screen Display joystick keyboard controller for PTZ Cam Camera, LCD display In-built multi-protocol maximum controllable 128 units PTZ camera 2D joystick controller etc. complete (Make: Sony or equivalent) | 1 | No.s
8 | LED TV 65 INCH Sony XBR-65X850E 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) w/ 3 Month Netflix Subscription, Sony AUTHORIZED DEALER - Includes Full Sony USA WARRANTY Sony 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) Go beyond what you've seen before with remarkable 4K HDR clarity, color and contrast. Scenes are more detailed, more natural and more real with 4K HDR Processor X1, and life's brilliance is revealed with extra smooth and vibrant colors INCLUDED IN THE BOX: Sony 65" Class (64.5" Diag.) LED 2160p Smart 4K Ultra HD TV with High Dynamic Range - AC power cord - Batteries - IR blaster - Owner's manual - Table top stand (separate, assembly required) - Voice remote control (RMF-TX300U) BUNDLE INCLUDES: Sony XBR-65X850E 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) | 1 | No.s
9 | RACK Supply, installation and fixing Wall Mount Network Server 19 Inch IT Cabinet Rack Enclosure Glass Door Lock, Dimensions: 20"H x 23.5"W x 18"D 130 pound weight capacity Included ground wire Fits Standard 19" rack-mount equipment Total Usable Space of 16" front to back (Make: NavePoint 9U or equivalent) | 1 | No.s
10 | Installation of various items and deviation items for complete work | 1 | No.s
11 | AMC Annual Maintenance Comprehensive | 1 | No.s
TOTAL

## MISCELL AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
BOQ OF MISCELLANEOUS ITEMS
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | LARGE LETTERS Providing and fixing Polish Stainless steel letter of Large Size (10" Height or of Size to be approved from Engineer Incharge) in Polish Stainless Steel of high grade that will not corrode in the environment of refinery. Light shall be long life and easy to maintain preferable of brands Philips or equivalent | 50 | No.s
2 | SMALL LETTER SIGNAGES Providing and fixing office signage at to of cabins, and all other rooms in polish stainless steel with letter size (1" or as advised) and design approved by the engineer incharge etc. complete | 25 | No.s
3 | NATURAL PLANTERS WITH CONCRETE POTS Providing and fixing natural planter out side building on 750 Dia on top of concrete pot of approved design by the engineer incharge, including full grown plant as approved by client etc. complete | 15 | No.s
4 | ARTIFICIAL PLANTERS WITH CERAMIC POTS Providing and fixing artificial planter with ceramic pot, white stone as approved by the engineer incharge | 50 | No.s
5 | WALL PAINTINGS Providing and fixing wall painting of approved make in various room with proper hanging arrangement in wall etc. complete | 45 | No.s
6 | LOCKER IN TOILETS Providing and fixing lockers in ladies toilet in Stainless Steel of minimum 8 nos and type of Godrej or Equivalent make etc. complete | 12 | No.s
7 | FIRE FIGHTING SYSTEM Providing and fixing proposed fire fighting system as per drawing as approved by architect or engineer including all necessary requirements for electrical, safety, approvals from local fire department etc. complete
| 1) Wet Sprinklers System | 1 | No.s
| 2) Dry Sprinklers System | 1 | No.s
| 3) Fire Hose Piping | 1 | No.s
| 4) Fire Alarm System | 1 | No.s
| 5) Fire Signage, Escape Routes etc. | 1 | No.s
8 | FOAM EXTINGUISHER Making and fixing concealed cabinets for fire / foam extinguisher at appropriate location with fire signage in a) Console room entry in ACP wall panels, b) Console Room curved partition, c) office corridor, d) Kitchen and Pantry, and d) Toilets or at locations as advised. | 40 | No.s
9 | TEMPARARY ELECTRICAL CONNECTION Providing and fixing permanent electric connection to building from local electrical office including cabling, sub meters, including preparation of load sheets, drawings etc. complete | 1 | No.s
10 | DIESEL GENERATOR SET Design, manufacture, supply at site, storing, handling, installation, testing and commissioning of following sizes of DG sets in sound proof enclosure (to meet the requirements of central pollution control board) as per specification complete in all respect 415Volts, 3 phase, 50 Hz, 1500 RPM AC alternator coupled to diesel engine complete with all accessories as per specifications tool kits, service manual, self starting device, fly wheel, coupling with guard, V belt, radiator cooling system, instrument panel, common bed plate, anti vibration isolation pads, grouting bolts, XLPE/PVC armoured cables and terminal box as per specification, adopter box, glands, nuts etc. first filling of Engine oil, Gear oil, high speed diesel oil, 24 volts chargeable battery set (Minimum 180 AH capacity) complete with batteries, battery charger etc. DG set including exhaust system, copper flexible expansion joints, silencer, fuel oil day tank, fuel oil piping, oil hand pump, steel support structure, logic panel (weather proof) with AMF operation, civil work etc. complete.
11 | It shall be salient with international noise international emission norms. It shall be compatible for basement as per norms. Any civil work for or necessary requirements shall be considered for basement installation. DG set include automatic switch during the power cuts. (Cummins/Kirloskar/ Volvo or Equivalent)
| 225 KVA | 1 | No.s
| 180 KVA | 2 | No.s
12 | METAL RATED FIRE DOORS Manufacturing, supplying, installation of metal fire door of approved color and make with door frame of material galvanized steel 2mm, of size standard Heights ( Wall Openings) 2100 mm with ador leaf in galvanized steel 1.6 mm thick, Infill with Rockwool thickness 45 mm, width 1200, fire Rating of120 Mins, hardware (all hardware parts are ISI marked), SS Hinges 4" x 12, SS D Handle 12", door Closer, dead lock with both side key, vision panel 300 x 300, fully flush construction with no visible welds, robust structure, ease of operation, maintenance-free & high level of aesthetic, including removal of existing doors, making surface good etc. complete | 4 | No.s
13 | PARITION IN 18 MM PLY Providing and fixing partitions in ant termite, moisture resistant ply with framing in aluminium pipe of 1" x 2" in vertical at 4' vertical intervals and 3' horizontal members, with 18 mm ply with 1 mm laminate (texture or glassy or plain) as approved by architect including making grooves, necessary beading, making edges, skirting etc, including making doors with all Hettich or equivalent accessories and door frame in necessary wooden section, polishing etc. complete | 100 | No.s
14 | PARITION IN ACP PANEL Providing and fixing partitions in 4 MM ACP panel both side laminate with framing in aluminium pipe of 1" x 2" in vertical at 4' vertical intervals and 3' horizontal members, with as approved by architect including making grooves, necessary beading, making edges, skirting etc, including making doors in ACP panel with all Hettich or equivalent accessories and door frame in necessary aluminium section etc. complete | 50 | No.s
15 | SOLAR SYSTEM Providing, supplying, installation and commissioning of appropriate design as approved by architect and engineer solar grid integrated system on roof top with solar PV module of ply crystalline silicon laminated with vacuum laminated glass of efficiency above 13% including mild steel module mounting structure (ms angle and ms flats) protected from corrosion with hot dip galvanized. Battery bank battery voltage 240 V DC of DOD allowed tubular battery 80% max, with efficiency 85%, capacity 240 V 350 Ah, tubular lead acid flooded electrolyte. Invertor of efficiency 90% +, solar charge controller, copper cables, all cables, MCB and accessories for integration with DG set and electric panel, etc. complete. Contractor to provide all design details in tender. | 1 | No.s
16 | WATER PROOFING TO WALL SURFACE Providing and applying water proofing treatment to vertical surface of basement and other walls, in all directions by using standard acrylic copolymer coating of Roff Hyguard, Monopoly 456, Dr. Fixit Pidilite 2K or equivalent in two coats including cleaning the surface by wire brush, washing and drying including covering guarantee of 10 years and as directed by Engineer In Charge etc. complete. |  | No.s
17 | LIGHTING ARESSTERS
A | Lightning arrestor station type 11KV grade | 4 | No.s
B | supplying and erecting earth pit of minimum bore dia. 150mm size, approved make Safe Earthing Electrode consisting Pipe-in-Pipe technology as per IS 3043-1987 made of corrosion free G.I. Pipes with constant ohmic value surrounded by highly conductive compound with high charge dissipation suitable for effective and maintenance free earthing as mentioned below :With 3 mtr. G.I. Pipes having outer pipe dia of 50mm having 80-200 micron galvanizing, Inner pipe dia. of 25mm having 200250 Micron galvanizing, connection terminal dia.of 12mm in nominal soil with 50 kg (Two Bag) Back filling Compound.
C | Covered copper wire (3 X 6 sq. mm) | 100 | Rmt
18 | PASSANGER LIFTS Proviiding and fixing passenger lifts in the hostel blocks with 12 persons capacity with approved speed as per the site conditions with grills gates, automatic breaking, electric panels etc. complete | 4 | No.s
19 | RO SYSTEN Providing and fixing RO system for the hostels with three levels filtration system to allow with approved make and model etc. complete | 4 | No.s
34 | LANDSCAPE WORKS Providing and supplying all the landscape work including paving, plants, lights, planters, construction in brick or concrete, approvals, detail design etc. complete | 1 | No.s
35 | EXTERNAL ELEVATION WORKS Providing and fixing Reckli formliner digitally printed concrete tiles in exterior including all the necessary support system as per approved design by Engineer Incharge, including making dummy models, design, mock-up up and approval of samples etc. complete | 1 | No.s
36 | LECTURE HALL WHITE BOARD Providing and fixing magnetic white board of the size 6 m x 4.5 m or more in approved material and quality with TW case border of more than 20 cm thick with arrangement of pens, duster, and supplying 4 set of four color pens and two dusters etc. complete | 2 | No.s
37 | LECTURE HALL PODIUM Providing and supplying lecture hall podium as per the approved design in marine ply with 1.0 to 1.5 mm approved texture laminate with glass work, electrical works etc. complete | 2 | No.s
38 | PROJECTOR SCREEN Providing and supplying projector screen of size 6 m x 4.5 m or more with manual closing system in approved material and quality etc. complete | 2 | No.s
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## VRV AUDI
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: AUDITORIUM
boq FOR HVAC SYSTEM
| Load | 476 | HP
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
A | HIGH SIDE WORKS
1 | OUTDOOR AND INDOOR UNITS Supply Installation, testing and commissioning of variable refrigerant flow modular type air conditioning system (Brand: Daikin or Mitsubishi or Toshiba or equivalent) with ODU shall have all DIP-IPM 100% inverter control Scroll compressors with step less modulation for precise control of frequency differential of 1Hz, having two stage oil separation to ensure complete oil recovery & more than 20 steps in ODU BLDC fan motor for stability of suction & discharge pressure and quick response to IDU temperature control suitable for 415 ±10% volts for outdoor and IDU comprises multispeed motor, D-X coil section, outer cabinet, individually controlled louver for Cassette and ducted units suitable to handle extent of duct work 230 ±5% volts for Indoor units. Complete with indoor and out door units ,accessories including fully charged with refrigerant R410A, units shall be suitable for operation on cooling as well as heating mode as per detail given in specifications for the following configurations :
Outdoor Units-Heat Pump Type
a | 14 HP | 16 | No.
b | 18 HP | 14 | No.
c | Multi Connecting Kits | 16 | No.
Indoor Units with Air Filter
a | Ceiling Mounted Cassette (Round Flow) 1.5 TR | 24 | Nos.
b | Ceiling Mounted Cassette (Round Flow) 2.0 TR | 4 | Nos.
c | Ceiling Mounted Cassette (Double Flow) 1.0 TR | 0 | Nos.
d | Ceiling Mounted Cassette (Double Flow) 1.5 TR | 17 | Nos.
e | Ceiling Mounted Cassette (Double Flow) 2.0 TR | 0 | Nos.
f | Ceiling Mounted Duct 1.0 TR | 0 | Nos.
g | Ceiling Mounted Duct 1.5 TR | 32 | Nos.
2 | CORDLESS REMOTE CONTROLS FOR INDOOR UNITS
| For Round Flow Cassette Type Unit Cordless Remote | 45 | Nos.
For Ductable Type Unit Cordless Remote
| For Ductable Type Unit Cordless Remote | 32 | Nos.
3 | CENTRAL REMOTE CONTROLLER Central remote Controller push button type for four floors: Integratable upto 64 remote controller groups & 160 indoor units can be controlled. In addition to basic controls such as settings for operation/stop, the operation mode & temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem.AN external input terminal is provided as standard. External signals enable the following function: central operation/stop, demand control, emergency stop, central operation output,& central alarm output. | 4 | Nos.
4 | COMMUNICATION CABLE Supply, installation and commissioning of communication cable with IDU including 15 Amp sockets of Legrand or equivalent with manufacturers specification cable, concealing in wall, piping, junction boxes in ceiling etc. complete (3C X 2.5SQMM) (Make: Polycab or equivalent) | 4500 | Rmtr.
5 | INSULATED REFRIGERANT PIPING Supply, fabrication, installation, testing of Interconnecting refrigerant pipe work with closed cell 19mm/13mm thick crosslinked polyethylene (XLPE) tubular insulation between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported with MS hanger as per manufacturer specification etc. complete | 1450 | Rmtr.
6 | Branch Distribution Joints | 250 | No.s
B | LOW SIDE WORKS
1 | AIR DISTRUBUTION Supply, Installation, Testing and commissioning of G.I.sheets metal factory fabricated duct complete with neoprene rubber gaskets, slip on flanges, vanes, Link levers, GI thread rod and perforated 'C' channel supports etc. in accordance with the approved shop drawings and specifications. | 150 | SqM
2 | VOLUME CONTROL DAMPERS Supplying, installing, and testing of Zero leakage Aluminium volume control damper within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system | 120 | sqmtr
3 | SUPPLY AIR GRILL Supply, installation, testing and commissioning of Powder coated Aluminium extruded grill with damper for supply and return air as per specification & the sizes will be as per schedules and drawing: | 25 | sqmtr
4 | RETURN AIR GRILL Supply, installation, testing and commissioning of Powder coated Aluminium extruded grill for supply and return air as per specification & the sizes will be as per schedules and drawing: | 25 | sqmtr
5 | SUPPLY AIR DIFFUSSER Supply, installation, testing and commissioning of Powder coated Aluminium extruded Diffuser for supply with damper as per specification & the sizes will be as per schedules and drawing: | 25 | sqmtr
6 | FLEXIBLE DUCT Supply, Installation, Testing and Commissioning of pre- insulated factory fabricated flexible ducts constructed out of aluminium sheet duly supported at regular interval as per site requirement. Ducts shall be of following sizes :
| 200 mm dia | 560 | Rmtr.
| 250 mm dia | 950 | Rmtr.
7 | SPIGOT Supply, installation, testing and commissioning of spigots of different sizes to facilitate flexible duct connection.
| 200mm dia | 185 | Nos.
| 250mm dia | 185 | Nos.
8 | CANVAS Supply, installation, testing and commissioning of fire retardant double layer flexible canvas cloth connection duly fitted on G.I. Frame with nut, bolt and washer between IDU and Duct etc complete as required. | 25 | Nos.
9 | LP PLENUM FOR SLOT DIFFUSER Supply, installation, testing and commissioning of factory fabricated GI LP Plenum for Multi slot diffuser for supply air duly fitted on G.I. Frame with nut, bolt and washer between diffuser and flexible duct etc complete as required.
| 1000mmx250mmx300mm | 195 | Nos.
10 | DRAIN PIPING (CPVC) 'Supply & installation, testing and commissioning of Rigid heavy class CPVC piping complete with fittings, supports as per specifications and duly insulated with 6 mm thick closed cell crosslinked polyethylene (XLPE) tubular insulation.
| 40 mm dia | 1200 | Rmtr.
| 32 mm dia | 1500 | Rmtr.
| 25 mm dia | 1200 | Rmtr.
11 | INSULATION Supply, fixing, installation, testing and commissioning of closed cell nitrile rubber/polyethylene foam, insulation on duct with adhesive dendrite and wrapped PVC tape insulation on joints compete as required.
| 25 MM thick | 1200 | sqmtr
12 | THERMAL PROTECTION Supply, installation, testing and commissioning of Thermal protecting layer over exposed duct/copper pipe insulation outer surface with approved make chemical and glass type as per specification compete as required. | 950 | sqmtr
13 | DUCT ACOUSTIC LINING Providing & fixing of acoustic insulation with open cell nitrile rubber sheet super silence of following thickness, on existing surface with adhesive/dentrite etc. complete as required. (As per specification).
| 10 mm thick | 450 | sqmtr
14 | SERVICE TRAP DOOR Supply, installation of service Trap door for Ducted IDU make of Aluminium composite panels(ACP) 3 mm thick of standard make on 25mmX25mm square pipe as per design requirement with required hanging arrangement in MS plat etc complete as requirement. | 50 | Nos
15 | CABLE TRAY Providing & fixing cable tray of appropriate size for running refrigerant piping along with control wiring etc. cable tray should be properly clamped and hang with all connected accessories.
| 300X100 GI Cable Tray | 500 | Rmtr.
| 400X100 GI Cable Tray | 400 | Rmtr.
16 | REFRIGERANT GAS Supply, charging, and commissioning of additional R-410a Gas charging on VRF system complete as required | 500 | Kg
17 | ELECTRICAL INSTALLATIONS Supply, installation, testing, and commissioning of Electrical Panel complete asper specification for VRF outdoor units, including stand, metal cabinet, etc. complete | 1 | Nos
6 AMPS MCB For Indoor Units
25 AMPS MCB For Indoor Units
40 AMPS MCB For Indoor Units
100MLAMPS ELCB IDU VRV System
300MLAMPS ELCB FOR ODU
18 | POWER CABLES FOR OUTDOOR UNITS Supply, laying, testing, and commissioning of following size armoured PVC insulated copper conductor FRLS Power and Control cable of following size on surface/recessed complete as required for VRF outdoor units
| 4 Corex 10 Sq.mm | 220 | Rmtr.
19 | MS STANDS Supply, installation and commissioning of outdoor unit table type (VRV) stands | 30 | No
20 | INDOOR UNITS HANGERS Supply, installation and commissioning of hangers for IDU with scaffolding, etc. complete | 145 | No
22 | DEVICATION & ADDITIONAL FEATURES |  | LS
ANNUAL COMPREHENSIVE MAINTENANCE CONTRACT Annual comprehensive maintenance contract of capacity for complete VRF system by OEM which cover all spare, software and consumables requirement to run the VRF system after expiring of 1 year(12 Months) defect liability period.
21 | For 1st year (0-12 Months) after expiring of 1 year(12 Months) defect liability period. | 12 | Mth
TOTAL OF HVAC WORKS

## ABS-BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
ABSTRACT BILL OF QUANTITIES (BOQ)
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
S/N | DISCRIPTION |  |  |  | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | THIRD FLOOR
2 | FOURTH FLOOR
3 | TERRACE FLOOR
4 | SANITATION WORKS
5 | ELECTRICAL WORKS
6 | CCTV SYSTEM
7 | MISCELLENIOUS
8 | SUB TOTAL
9 | TOTAL | [5 empty] | 0
|  | Conversion Rate: | 65.33 | USD |  | Dt.: 13-11-2017

## 3F BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ FOR THIRD FLOOR
ABSTRACT
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING FLOORING AND PAVING Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 365.4798 | CuM
2 | DISMANTLING CONCRETE MEMBERS SLAB, STAIRCASE, BEAMS, COLUMNS OR WALLS Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 55 | CuM
3 | DISMANTLING LANDSCAPE WORK Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 110 | Cum
4 | DISMANTLING BRICK WALLS Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 150 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 560.4798 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 2283.6842 | SqM
7 | REMOVING OLD PAINT AND MAKING SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 1011.5258 | SqM
8 | RCC COLUMNS Providing and laying in position cement concrete in RCC columns for reinforced cement concrete work, using cement content as per approved design mix etc. complete. | 135.4657 | CuM
9 | RCC SLAB Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 41.3355 | CuM
10 | RCC WAIST SLAB Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 6.16 | CuM
11 | CENTERING AND SHUTTERING Centring and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 358.3461 | SqM
12 | HYSD REINFORCEMENT Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 12807.2857 | Kg
13 | AERATED CEMENT BLOCKS Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineer-in-Charge. (The payment of RCC band and reinforcement shall be made for separately). | 784.5996 | CuM
14 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 78.46 | SqM
15 | INTERNAL PLASTER FOR REPAIR OF SPALLING IN SLABS, BEAMS AND COLUMNS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 1011.5258 | SqM
16 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 0 | SqM
17 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 250.8 | SqM
18 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 509.6646 | SqM
19 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 411.2237 | SqM
| SIZE: 800 X 800 (Avg.) | 164.4895 | SqM
| SIZE: 600 X 1200 (Avg.) | 164.4895 | SqM
20 | MS FABRICATION WORK FOR REPAIR, JACKETING STRUCTURAL MEMBERS ETC. Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 202.3052 | SqM
21 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws(including necessary handles, knobs, locks, tower bolt stopper etc. complete | 351.54 | SqM
22 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm | 329.56 | CuM
23 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 1011.5258 | SqM
24 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 0 | SqM
25 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of ACMS. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. | 58 | No.s
26 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete
|  | 58 | No.s
27 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Conf. Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). | 58 | No.s
28 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 50 | SqM
29 | MODULAR KITCHEN PLATFORM FOR PANTRY Providing and fixing Modular kitchen as per drawings with polished Stainless Steel platform with large size Stainless Steel wash basin with S trap and cleaning Jali. Modular kitchen will be made form 18 mm thick marine ply with glazed finished laminates of white and black colors with Hettich fittings of auto swing/close type. Internal wet and dry arrangement shall be made with use of Stainless Steel trays with all system for crockery, utensils, spoons, knifes etc. complete. Framing of the modular kitchen shall be in MS pipes with pure polyester coating from inside and outside. Powered coating shall be provided above pure polyester coat of approved quality, color, micron etc. complete. Kota stone base shall be provided to the SS platform. Proper slope for drain in Platform and floor shall be provided with Nahani trap. Electrical points at suitable locations shall be provided at suitable locations. | 0 | No
Additional glass cookery cabinet on wall above platform of approved quality and as per design shall be provided. electronic exhaust chimney of approved make shall be provided by the contractor. Any additional requirements shall be clarified before quoting for this item.
30 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | No.s
31 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 25 | No.s
32 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 4 | No.s
33 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 4 | No.s
34 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 4 | No.s
35 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 14.256 | SqM
36 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 9.072 | Nos
37 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. | 50 | SqM
38 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete | 50 | SqM
39 | REPAIR OF ENTRANCE PORTCH Repair of entrance porch by water proofing in bitumen with tile finish on top surface (as per water proofing specifications), replacement of old drainage with new drainage system, including painting, re concreting the floor etc. complete | 4 | No.s
40 | PANTRY PLATFORM Providing and fixing pantry platform in traditional Indian design in front of auditorium entry as approved by architect or engineer in Corian and MR 18mm play with internal lighting, glass work etc. complete | 4 | No.s
41 | CABINATE IN PANTRY Providing and fixing 3.2 m (l) x 0.45 (w) x 3.0 (h) cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 4 | No.s
42 | EXTERIOR CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. | 150 | LS
43 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 250 | SqM
44 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete | 250 | No.s
TOTAL

## 4F BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ FOR FOURTH FLOOR
ABSTRACT
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING FLOORING AND PAVING Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 365.4798 | CuM
2 | DISMANTLING CONCRETE MEMBERS SLAB, STAIRCASE, BEAMS, COLUMNS OR WALLS Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 55 | CuM
3 | DISMANTLING LANDSCAPE WORK Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 110 | Cum
4 | DISMANTLING BRICK WALLS Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 30 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 560.4798 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 2283.6842 | SqM
7 | REMOVING OLD PAINT AND MAKING SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 4936.1028 | CuM
8 | RCC COLUMNS Providing and laying in position cement concrete in RCC columns for reinforced cement concrete work, using cement content as per approved design mix etc. complete. | 181.0194 | Cum
9 | RCC SLAB Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 31.3706 | Cum
10 | RCC WAIST SLAB Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 6.16 | Cum
11 | CENTERING AND SHUTTERING Centring and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 1546.3958 | SqM
12 | HYSD REINFORCEMENT Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 15298.499 | Kg
13 | AERATED CEMENT BLOCKS Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineer-in-Charge. (The payment of RCC band and reinforcement shall be made for separately). | 1092.1787 | CuM
14 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 109.2179 | SqM
15 | INTERNAL PLASTER FOR REPAIR OF SPALLING IN SLABS, BEAMS AND COLUMNS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 4936.1028 | SqM
16 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 0 | SqM
17 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 2471.9703 | SqM
18 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 741.5911 | SqM
19 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 513.613 | SqM
| SIZE: 800 X 800 (Avg.) | 205.4452 | SqM
| SIZE: 600 X 1200 (Avg.) | 205.4452 | SqM
20 | MS FABRICATION WORK FOR REPAIR, JACKETING STRUCTURAL MEMBERS ETC. Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 987.2206 | SqM
21 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws(including necessary handles, knobs, locks, tower bolt stopper etc. complete | 427.14 | SqM
22 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm | 400.4 | CuM
23 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 4936.1028 | SqM
24 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 0 | SqM
25 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of ACMS. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. | 88 | No.s
26 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete
|  | 88 | No.s
27 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Conf. Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). | 88 | No.s
28 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 50 | SqM
29 | MODULAR KITCHEN PLATFORM FOR PANTRY Providing and fixing Modular kitchen as per drawings with polished Stainless Steel platform with large size Stainless Steel wash basin with S trap and cleaning Jali. Modular kitchen will be made form 18 mm thick marine ply with glazed finished laminates of white and black colors with Hettich fittings of auto swing/close type. Internal wet and dry arrangement shall be made with use of Stainless Steel trays with all system for crockery, utensils, spoons, knifes etc. complete. Framing of the modular kitchen shall be in MS pipes with pure polyester coating from inside and outside. Powered coating shall be provided above pure polyester coat of approved quality, color, micron etc. complete. Kota stone base shall be provided to the SS platform. Proper slope for drain in Platform and floor shall be provided with Nahani trap. Electrical points at suitable locations shall be provided at suitable locations. | 0 | No
Additional glass cookery cabinet on wall above platform of approved quality and as per design shall be provided. electronic exhaust chimney of approved make shall be provided by the contractor. Any additional requirements shall be clarified before quoting for this item.
30 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | No.s
31 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 25 | No.s
32 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 4 | No.s
33 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 4 | No.s
34 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 4 | No.s
35 | POWDER COATED ALLUMINUM LOUVERED WINDOWS IN TOILETS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 31.968 | SqM
36 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 20 | Nos
37 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. | 50 | SqM
38 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete | 50 | SqM
39 | REPAIR OF ENTRANCE PORTCH Repair of entrance porch by water proofing in bitumen with tile finish on top surface (as per water proofing specifications), replacement of old drainage with new drainage system, including painting, re concreting the floor etc. complete | 4 | LS
40 | PANTRY PLATFORM Providing and fixing pantry platform in traditional Indian design in front of auditorium entry as approved by architect or engineer in Corian and MR 18mm play with internal lighting, glass work etc. complete | 4 | LS
41 | CABINATE IN PANTRY Providing and fixing 3.2 m (l) x 0.45 (w) x 3.0 (h) cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 4 | No.s
42 | EXTERIOR CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. | 150 | Sq.M
43 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 250 | Sq.M
44 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete | 250 | Sq.M
TOTAL

## TR BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ FOR TERRACE FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 2135.04 | CuM
2 | ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 151.2 | SqM
3 | BRICK WORK Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 45 | CuM
4 | WATER PROOF CEMENT PAINT Providing and applying two coats of waterproof cement paint of an approved make and colour as per manufacturers specifications to smooth sand faced or other surfaces, upto 10m height from ground level and at all locations as directed including preparing surfaces for painting by any approved means, watering, scaffolding, cleaning and curing etc. complete as directed by Engineer-in-charge. | 40.7818 | SqM
5 | UPVC PIPES AND BENDS Providing and fixing UV resistant self fit UPVC pipes of approved make for Rainwater down takes confirming to IS 13592:1992 Type A suitable for 4kg/sqcm pressure for following pipe diameters including rain water receiving recess with pvc plug bend necessary fittings such as offsets shoes, fixing the pipes on wall with clips filling the joints with solvent/cement and necessary scaffolding etc. complete as directed by Engineer In Charge. 150mm dia | 150 | Rmt
6 | WATER PROOFING TO TERRACE Providing water proofing treatment of Old Terraces by removing existing treatment. Sealing of cracks by non shrink cracks fill compound by applying first coat of polymer modified semi-viscous paste prepared by mixing polymer of approved make (such as Aquatek conchem/ Master Seal 550/brush bond / RoffSupercrete/ Webercrete/ Monobond / Perma shield / Hypercrate / Master Crete M 81/ MC-Bauchemie) and Cement in 1:2proportion ( 1 litre polymer : 2 Kg Cement) or Rohnex water proofing system in two coats(1kg powder,700 ml water and polymer jelly for first coat & 1 kg powder,500 ml water & polymer jelly for second coat) to a neatly cleaned and dust free concrete surface and upto 300 mm over parapet wall prepared by removing loose and deposited material with brush and water, laying glass fibre mesh of 10 x 10 specification of approved make over tacky surface of first coat of polymer followed by second coat in transverse direction, laying mechanical protective cover to polymer coating treatment with brick bat coba with burnt broken brick bats laid in C.M. 1:5 admixed with approved water proofing compound, filling up to half depth of brick bats, curing this layer for 3 days, | 31.3706 | Sq.M
applying cement slurry over this layer joints of brick bats with C.M. 1:3 admixed making the Sq.m. 1102.00 219.00 junctions at the parapet rounded and tapered top for required height, with drip mould at the junction of plaster and parapet and curing and covering 7 years Guarantee against leak proofness on court including ponding test etc. complete (Make: Dr. Fixit Roofseal or equivalent)
7 | GROUTING TO VARIOUS PARTS Providing Grouting by specially prepared grout of Weber Crete /Roff Supercrete /Polyalk P/Monobond /Perma shield/Hypercrate or equivalent with cement in proportion 1:3.5 (1 part chemical & 3.5 part cement by weight) along with 50 ml super plasticizer Roff Plast 320/sun polycrete NCT/Perma Plast/Supercon 100 or non shrinking, non cracking antiwash high strength polymer cement grout P C grout available in bags or equivalent with proper water for injectable consistency and applying it in the body of structure like slab, beam, column, pillars, deckslab, retaining wall, basement, underground and elevated water storage reservoir concrete and brick wall, crack portion of structure etc. by injectng method, to achieve its original strength including drilling of suitable diameter drills holes at 2 to 4 Nos. per sqm. using caps and nozzle grouting machinery necessary, scaffolding, finishing and covering gurantee of 10 years and necessary testing etc. complete. | 250 | Kg
8 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 250 | SqM
TOTAL

## SANI BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ FOR SANITATION WORK FOR ALL FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | WHITE COLOR WATER CLOSET Providing & Fixing star white color vitreous China wall mounted water closet with heavy duty soft close seat cover & concealed dual tank. Complete with all accessories like pipes, cistern etc. including cutting & making good wall & floor wherever required. (Model PERRYWARE PETIT S OR Equivalent Standards Dimension: 380*360*545 or more) | 38 | No
2 | WHITE COLOR WASH BASIN OVAL SHAPE Providing & Fixing star white color vitreous China wash basin Oval shape, 32mm dia C.P waste, 32mm Dia C.P wall flange & rubber adopter for waste connection complete, including cutting & making good the walls wherever required. (Model - Perryware Cascase NXT BC Basin or Equivalent Dimension: 555 x 450 x 205 or more) Note: Contractor shall approve the make and design from Engineer Incharge. | 15 | No
3 | WHITE COLOR URINAL Providing & Fixing star white color vitreous China urinal with inbuilt auto flush system with s.s. bracket, pipe to wall with C.P flange compete including cutting & making good the walls & floors wherever required. Model Perryware New Magnum Standard Urinal, or Equivalent, Dimension: 380*400*590 or more) Note: Contractor shall approve the make and design from Engineer Incharge. | 9 | No
4 | STAINLESS STEEL SINK Providing & Fixing in position best stainless steel sinks with 40mm C.P. brass waste chrome plated & s.s. waste pipe. complete in all respect including cutting & making good the walls & floors. in canteen. Jaguar/Sunfold/Equivalent 24"X20"X8" 1.0mm thick mat finish. Note: Contractor shall approve the make and design from Engineer Incharge ACMS | 2 | No
5 | WALL MOUNTED TAP Providing & Fixing chrome plated wall mounted taps over wash basin complete in all respect including cutting & making good the walls wherever required (Make: As approved by the Engineer Incharge) | 21 | No
6 | STOP TAP FOR WATER CLOSET Providing & Fixing 15mm C.P brass bib tap for water closet with C.P brass threaded flange complete, including cutting & making good the walls wherever required. Model - : Contractor shall approve the make and model form Engineer Incharge | 38 | No
7 | ANGLE VALVE FOR WATER CLOSET Providing & Fixing 15mm C.P. brass angle valve with C.P copper connecting pipe 375mm long & nuts, washer & C.P. brass flange complete, including cutting & making good the wall wherever required. JAQUAR CONTINENTAL 053 KN for water closet cistern & basins. or Equivalent in Kohler/TOTO/American Standards | 38 | No
8 | STOP COCK FOR URINAL BEFORE SENSOR Providing & Fixing concealed stop cocks for cold water supply. Note: Contractor shall approve the make and design from Engineer Incharge ACMS | 38 | No
9 | BRASS MIXING FITTING FOR SINK Providing & Fixing 15mm C.P. brass mixing fitting for sink with swinging spout complete, including cutting & making good the walls wherever required. Wall mixer with swivel spout. Note: Contractor shall approve the make and design from Engineer Incharge ACMS | 38 | No
10 | AUTOMATIC SOAP DISPENSER Providing & Fixing ABS body automatic liquid soap dispenser for all was basins with liquid soaps. Note: Contractor shall approve the make and model from Engineer Incharge ACMS) | 17 | No
11 | CROMIUM PLATED TOWEL ROD 16 MM DIA Providing and fixing chromium plated towel rod 16 mm dia. and 75 cm. in length including all accessories, fitting, cleaning, etc. complete. | 14 | No
12 | PVC NAHANI TRAP Providing and fixing 150 cm Rigid PVC Nahani Trap including PVC grating, bend, connecting piece of P.V.C.pipe of required diameter, pipe up to the outside face of the wall, making good the holes and repairs, testing, including cover etc. complete. | 40 | No
13 | MIRROR IN TOILET Providing and fixing 2000 mm x 900 mm size superior type mirror with 16 mm dia including chromium plated towel rod etc. complete. Note: Contractor shall approve a sample from architect/engineer incharge | 38 | No
14 | PIPE FOR DRAINAGE Providing and fixing in position Heavy type alkathene pipe for drainage connections including cutting, boring holes in wood work or masonry if necessary, making connections of pipe to sink and giving test for no leakages, making good the damaged surface etc. complete. As directed by Engineer in-charge
| 25 MM Dia | 3000 | Rmt
| 40 MM Dia | 2500 | Rmt
15 | PIPE FOR RAINWATER DRAINAGE Providing and fixing in position Heavy type alkathene pipe for drainage connections including cutting, boring holes in wood work or masonry if necessary, making connections of pipe to sink and giving test for no leakages, making good the damaged surface etc. complete. As directed by Engineer in-charge ACMS.
| 250 MM Dia | 750 | Rmt
16 | UPVC WASTE PIPE Providing and fixing UPVC waste pipes for Wash Basin / Urinals including all fittings, making chases in wall / floor and reinstating the surface. etc. complete. As directed by Engineer in-charge ACMS.
| 50 mm Dia | 750 | Rmt
| 40 MM Dia | 1500 | Rmt
17 | PVC PIPE Providing, cutting, erecting, jointing, clamping, fixing including making clamping, fixing including making opening in walls, floors, S.W.R., P.V.C. pipe and fittings, such bends, elbows single junction, double junctions, cowls with PVC / G.I. brackets etc. including jointing with solvent cement/rubber ring, making necessary holes in masonry / concrete, all installation as workmanship like manner and as per manufacturer's instructions, testing, commissioning the lines, attending to leakage if any making it to good leakage if any making it to good condition. Following diameters of S.W.R.PVC pipe and fittings of approved make conforming to IS 13592-1992. All as directed.
| 110 mm. dia. PVC pipe for soil stack | 350 | Rmt
| 75 mm. dia. PVC pipe for waste wear pipe | 250 | Rmt
| 50 mm. dia. PVC pipe for anti-symphonic pipe | 75 | Rmt
18 | RECTANGULER TISSUE PAPER HOLDER FOR LADIES AND GENT TOILET Providing and fixing rectangular tissue paper holder in ladies and gents toilet for holding hand wash tissue papers, with additional storage facilities etc. complete (Model: As approved by Engineer Incharge) | 38 | No
19 | TOILET TISSUE PAPER HOLDER Providing and fixing toilet tissue paper holder in ladies and gents toilet for holding hand wash tissue papers, with additional storage facilities etc. complete (Model: As approved by Engineer Incharge) | 38 | No
20 | WATER TANK Providing and fixing PVC tank of appropriate capacity in basement, roof and other places etc. complete | 15000 | Ltrs |  |  |  | `
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## ELE BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ FOR ELECTRICAL WORK FOR ALL FLOORS
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | POINT WIRING FOR INDEPENDENT PLUG Providing, fixing and testing point wiring for independent plug in 20 mm rigid PVC conduit with 1.5 sqm FRLS grade Copper wire with modular switch and concealed wiring with necessary joints, and required accessories complete. As directed by Engineer in-charge | 430 | No
2 | LIGHT POINT WITH SINGLE MODULER SWITCH Providing, fixing and testing light point with single modular switch with concealed cables and modular plate etc. complete. | 467 | No
3 | POINT WIRING FOR WALL MOUNTED FANS Providing, fixing and testing point wiring for wall mounted fans in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade Copper wire with flush type switch and required accessories etc. complete. | 253 | No
4 | CEILING FANS Providing, supplying and fixing ceiling fans of with regulator and all other accessories, etc. complete (Make: Bajaj or equivalent) | 104 | No
5 | LED BATTEN LIGHTS Supply, Installation, testing & commissioning of the 36 watt or above, concealed LED circular light fixture in console room complete with copper choke, starter, LED etc. (Make PHILIPS Mirolta Pro r16 36 Watts LED Batten - High Power High Performance Tube Light - Cool Day Light or equivalent) | 154 | No
6 | CEILING CIRCULER LIGHT PANEL Supply, installation, testing & commissioning of white color ceiling fixture of material metal and glass with 15 watt or above LED light including, started, LED system, switches etc, complete (Make: Philips myLiving canvas white model no. 77050/31/16 or equivalent) | 50 | No
7 | STEPS AND RAMP LIGHTING Supply, Installation, testing & commissioning for steps in auditorium, steps, below seats and ramp lighting of the watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania: wall 5 STE DIR 4W LED WHT LLB with switches etc. | 150 | No
8 | PENDENT LIGHT IN LOBBY Providing, installation, testing & commissioning of 6-1/2’’ Pendalyte with Satined Aluminium Reflector, with suspended, lamp holder, LED/CFL lamp of 32 watt and above etc. complete (Make: Philips Pendalyte with Satined Aluminium Reflector or equivalent) | 10 | No
9 | HANGING LIGHT FIXTURES FIXTURE Supply, Installation, testing & commissioning hanging light fixtures in lotus shape made from brass of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested
| Large | 5 | No
| Small | 5 | No
10 | WALL LED LIGHT Providing, supplying, installation as commissioning, regular 26 watt and above light fixtures with light holder of approved quality including concealed cabling, modular switch, texted as approved by engineer, with wiring, scaffolding, etc. complete (PHILIPS 26-watt LED Bulb ¦AceBright High Wattage LED Bulb Base: B22 Light Bulb for Home ¦ Crystal White or equivalent) | 25 | No
11 | WALL MOUNTED FIXTURE Supply, Installation, testing & commissioning for curved wall in console room of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested | 10 | No
12 | LED TUBE ON TERRACE Supply, installation, testing and commission of LED tube25 watt or above of material glass and plastic including bulb, clips, LED system, civil work etc complete(Make: Philips Linea 26-Watt LED Tube (White) or equivalent) | 10 | No
13 | LED STRIP LIGHTS Supply, installation, testing and commissioning of LED strip lights 8 watt above per metre of required color or hue including, adaptor, controller, male-female clips, cable, switches etc. complete in ceiling, tables, with scaffolding, glass etc. complete. (Make: Philips 800284 Hue Light strip Plus, 2Nd Generation or equivalent) | 50 | No
14 | EXTERIOR LED LIGHTS FOR BUILDING Supply, Installation, testing & commissioning for lights in exterior in elevation of LED or compliance concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. Contractor shall assign specialised company for design and installation of external lighting with previous experience in similar field. Contractor and subcontractor shall approve the design for external lighting from architect or engineer any suggestions shall be incorporated with all necessary requirement etc. complete This item include AMC for three years.. | 1 | No
15 | POINT WIRING FOR LAN POINTS Point wiring for LAN points will be carried out with CAT 6, LAN Cable, in surface/ recessed existing PVC conduits, inclusive of p/f of G.I/ PVC box & modular plate RJ 45 AT&T LAN socket. Work includes cutting & repair of chase to original finish. (Make of cable: Polycap or equivalent) | 50 | No
16 | CIRCUIT WIRING Supply and wiring wall / floor etc. / recessed / surface as per colour code with the following size PVC Insulated copper wire along with given earth wire for phase neutral and earth conductor with standard colour coding, through ISI marked rigid PVC conduit of given size with all accessories. The rate includes the cost of complete wiring from switch box to switch box etc. complete (Make of wire: Polycap or equivalent)
a. | 2 x 1.0 Sqmm PVC Copper wire in 20 mm dia conduit for Emergency Stop Box Connection | 1500 | Metre
b. | 3 x 1.5 Sqmm PVC Copper wire with in 20 mm dia conduit (The rate includes the cost of complete wiring between individual switch boards) | 1500 | Metre
c. | 3 x 2.5 Sqmm PVC Copper wire with in 20 mm dia conduit (for lighting main circuit, 15A plug points & UPS point wiring & 1T AC) | 1500 | Metre
d. | 5 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 3-Ph circuits like 3-Ph AC / UPS) | 1500 | Metre
e. | 3 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 1.5/2Tonne AC and UPS I/P & O/P upto UPS O/P DB and for Sign Boards if there are multiple Name boards) | 1500 | Metre
17 | AC/HEATER METAL BOX Supplying and fixing for AC/Heater metal box of GI box with modular plate and cover in front on surface or in recess , including providing and fixing of 3 No's 3 pin 5/6 amps modular socket outlet and 15/16 amps. Modular switch, connections, painting etc. as required | 154 | No
18 | TWO WAY CONNECTIONS Point wiring for two way connects for switching lights in corridor, toilet, landscape, steps in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade copper wire with flush type switch and required accessories. | 50 | No
19 | UTP NETWORK CABLE CAT 6 Supplying & installing UTP networking Cat-6+ cable suitable for LAN / WAN Computer networking. | 50 | No
20 | M. S. CABLE TRAY Fabrication and installing required sizes of perforated M.S. cable trays including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with M.S. suspenders and including painting with powder coating etc. as required. | 1 | No
21 | DISTRUBUTION BOARD Distribution board of approved make as per design requirements of Legrand or equivalent make with MCB cables, separation for computers, lights etc. complete | 16 | No
22 | PVC CABLE Supply and erecting PVC armoured cable 2 core 2.5 sq. mm stranded/solid copper conductors continuous 5.48 sq. mm (12 swg) GI earth wire complete erecting with glands & lugs on wall in trenches complete (Measurement to be as per site condition and location of Mains) (Make: Polycap or equivalent) | 1500 | Metre
23 | SUPPLY 16" EXHAUST FAN Supply of 16" exhaust fan of PVC of high speed with installation, testing including aluminium or wooden framing etc. complete. (Make Godrej/Philips or equivalent) Note: Contractor shall approve the make and model from Engineer in-charge of ACMS) | 32 | No
24 | BELL POINTS Providing and fixing bell points with concealed conduits with cable, bell of approved make, modular switches, etc. complete | 6 | No
25 | TELEPHONE POINTS Providing and fixing telephone points with modular plate, cable, switch with concealed cabling etc. complete | 20 | No
26 | EARTHLING WITH G.I. EARTH PIPE Earthling with G.I. earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but without charcoal or coke and salt) as required. | 25 | No
27 | MUSIC CUM PA SYSTEM OF PHILIPS MAKE Providing and fixing music systems of Philips make with speakers, CD, USB, Radio etc. complete as approved by engineer incharge with stereo speakers in appropriate locations, including stereo head phones etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge ACMS. Design & product detail to be submitted with tender. | 4 | No
28 | MODULAR KITCHEN HOT PLATE Providing and fixing modular kitchen hot plate with 4 no. of coils of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge ACMS. | 4 | No
29 | MODULAR KITCHEN GRILL AND OVEN Providing and fixing modular kitchen grill and oven of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge ACMS. | 4 | No
30 | MODULAR KITCHEN FRIDGE Providing and fixing modular kitchen fridge of approved size and capacity Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer incharge ACMS. | 4 | No
31 | WATER HEATER Supplying, installation, and testing Smith-Jaguar water heater with all accessories in Male and Female toilets complete. (Make: Jaguar CEWHR-DIGITAL Digital with remote & dual heating elements 35 19.00 395X760 1 KW/ 1.5 KW/ 2.5 KW) | 32 | No
32 | ELECTRICAL PANEL Suppling, installation, commissioning of main electrical panel in basement for all electrical equipments with all necessary requirements as approved by architect or engineer etc. complete. | 4 | No
33 | LANDSCAPE LIGHTS Providing and fixing landscape lights with fixture of approved make and models as per the design with weather protection of Philips or equivalent make with connections, installation etc. complete | 20 | No
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## CCTV BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ FOR CCTV SYSTEM
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DOME CAMERAS Supply Installation ,Testing & Commissioning for cctv Camera, Specification: High Resolution Digital Image Sensor HIKVISION 5 MP Indoor Dome CCTV Camera with inbuilt Audio Mic DS-2CE76H0T-ITPFS + USEWELL BNC/DC, White Wired, 1080P Image Sensor (Make: HIKVISION or Equivalent) | 20 | No.s
2 | BULLET CAMERAS Supply Installation Testing & Commissioning for cctv camera, Specification: HIKVISION 2MP Eco HD 1080P Night Vision Bullet Outdoor Wired CCTV Camera for 2MP & Above DVRs, White (Model: Hikvision or Equivalent) | 4 | No.s
3 | PTZ CAMERAS Supply installation and commissioning of CCTV camera etc. complete ( Make: HIKVISION 2-inch 4 MP Color Mini PT Dome Network Camera DS-2DE2C400SCG-E Compatible with JK Vision BNCor Equivalent) | 1 | No.s
4 | CONNECTOR FOR CCTV CAMERAS Connector for cctv camera, adaptor, | 25 | No.s
5 | NETWORK VIDEO RECORDER Supply, installation and commissioning of NVR:64 Channel 4K NVR, Plug And Play Black, Up to 8 SATA interfaces Third-party network cameras supported Up to 12 Megapixels resolution recording Support various VCA detection alarm and VCA search Support HDD hot swap with RAID0,1,5,6,10 storage scheme configurable etc. complete (Make: Hikvision DS-9664NI-I8 or equivalent) | 4 | No.s
6 | CAT 6 CABLE Cat 6 Cable including making hole, taking though ceiling though pipe, concealing, scaffolding etc. complete | 900 | Rmt
7 | JOYSTICKS FOR CCTV CAMERAS CCTV LCD Screen Display joystick keyboard controller for PTZ Cam Camera, LCD display In-built multi-protocol maximum controllable 128 units PTZ camera 2D joystick controller etc. complete (Make: Sony or equivalent) | 1 | No.s
8 | LED TV 65 INCH Sony XBR-65X850E 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) w/ 3 Month Netflix Subscription, Sony AUTHORIZED DEALER - Includes Full Sony USA WARRANTY Sony 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) Go beyond what you've seen before with remarkable 4K HDR clarity, color and contrast. Scenes are more detailed, more natural and more real with 4K HDR Processor X1, and life's brilliance is revealed with extra smooth and vibrant colors INCLUDED IN THE BOX: Sony 65" Class (64.5" Diag.) LED 2160p Smart 4K Ultra HD TV with High Dynamic Range - AC power cord - Batteries - IR blaster - Owner's manual - Table top stand (separate, assembly required) - Voice remote control (RMF-TX300U) BUNDLE INCLUDES: Sony XBR-65X850E 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) | 1 | No.s
9 | RACK Supply, installation and fixing Wall Mount Network Server 19 Inch IT Cabinet Rack Enclosure Glass Door Lock, Dimensions: 20"H x 23.5"W x 18"D 130 pound weight capacity Included ground wire Fits Standard 19" rack-mount equipment Total Usable Space of 16" front to back (Make: NavePoint 9U or equivalent) | 1 | No.s
10 | Installation of various items and deviation items for complete work | 1 | No.s
11 | AMC Annual Maintenance Comprehensive | 1 | No.s
TOTAL

## MISCELL BH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: BOYS HOSTEL (BLOCK 1, 2, 3 AND 4)
BOQ MISCELLANEOUS ITEMS
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | LARGE LETTERS Providing and fixing Polish Stainless steel letter of Large Size (10" Height or of Size to be approved from Engineer Incharge) in Polish Stainless Steel of high grade that will not corrode in the environment of refinery. Light shall be long life and easy to maintain preferable of brands Philips or equivalent | 10 | No.s
2 | SMALL LETTER SIGNAGES Providing and fixing office signage at to of cabins, and all other rooms in polish stainless steel with letter size (1" or as advised) and design approved by the engineer incharge etc. complete | 20 | No.s
3 | NATURAL PLANTERS WITH CONCRETE POTS Providing and fixing natural planter out side building on 750 Dia on top of concrete pot of approved design by the engineer incharge, including full grown plant as approved by client etc. complete | 10 | No.s
4 | ARTIFICIAL PLANTERS WITH CERAMIC POTS Providing and fixing artificial planter with ceramic pot, white stone as approved by the engineer incharge | 15 | No.s
5 | WALL PAINTINGS Providing and fixing wall painting of approved make in various room with proper hanging arrangement in wall etc. complete | 10 | No.s
6 | LOCKER IN TOILETS Providing and fixing lockers in ladies toilet in Stainless Steel of minimum 8 nos and type of Godrej or Equivalent make etc. complete | 20 | No.s
7 | FIRE FIGHTING SYSTEM Providing and fixing proposed fire fighting system as per drawing as approved by architect or engineer including all necessary requirements for electrical, safety, approvals from local fire department etc. complete
| 1) Wet Sprinklers System | 1 | No.s
| 2) Dry Sprinklers System | 1 | No.s
| 3) Fire Hose Piping | 1 | No.s
| 4) Fire Alarm System | 1 | No.s
| 5) Fire Signage, Escape Routes etc. | 1 | No.s
8 | FOAM EXTINGUISHER Making and fixing concealed cabinets for fire / foam extinguisher at appropriate location with fire signage in a) Console room entry in ACP wall panels, b) Console Room curved partition, c) office corridor, d) Kitchen and Pantry, and d) Toilets or at locations as advised. | 0 | No.s
9 | TEMPARARY ELECTRICAL CONNECTION Providing and fixing permanent electric connection to building from local electrical office including cabling, sub meters, including preparation of load sheets, drawings etc. complete | 1 | No.s
10 | DIESEL GENERATOR SET Design, manufacture, supply at site, storing, handling, installation, testing and commissioning of following sizes of DG sets in sound proof enclosure (to meet the requirements of central pollution control board) as per specification complete in all respect 415Volts, 3 phase, 50 Hz, 1500 RPM AC alternator coupled to diesel engine complete with all accessories as per specifications tool kits, service manual, self starting device, fly wheel, coupling with guard, V belt, radiator cooling system, instrument panel, common bed plate, anti vibration isolation pads, grouting bolts, XLPE/PVC armoured cables and terminal box as per specification, adopter box, glands, nuts etc. first filling of Engine oil, Gear oil, high speed diesel oil, 24 volts chargeable battery set (Minimum 180 AH capacity) complete with batteries, battery charger etc. DG set including exhaust system, copper flexible expansion joints, silencer, fuel oil day tank, fuel oil piping, oil hand pump, steel support structure, logic panel (weather proof) with AMF operation, civil work etc. complete.
11 | It shall be salient with international noise international emission norms. It shall be compatible for basement as per norms. Any civil work for or necessary requirements shall be considered for basement installation. DG set include automatic switch during the power cuts. (Cummins/Kirloskar/ Volvo or Equivalent)
| 225 KVA | 0 | No.s
| 180 KVA | 0 | No.s
12 | METAL RATED FIRE DOORS Manufacturing, supplying, installation of metal fire door of approved color and make with door frame of material galvanized steel 2mm, of size standard Heights ( Wall Openings) 2100 mm with ador leaf in galvanized steel 1.6 mm thick, Infill with Rockwool thickness 45 mm, width 1200, fire Rating of120 Mins, hardware (all hardware parts are ISI marked), SS Hinges 4" x 12, SS D Handle 12", door Closer, dead lock with both side key, vision panel 300 x 300, fully flush construction with no visible welds, robust structure, ease of operation, maintenance-free & high level of aesthetic, including removal of existing doors, making surface good etc. complete | 2 | No.s
13 | PARITION IN 18 MM PLY Providing and fixing partitions in ant termite, moisture resistant ply with framing in aluminium pipe of 1" x 2" in vertical at 4' vertical intervals and 3' horizontal members, with 18 mm ply with 1 mm laminate (texture or glassy or plain) as approved by architect including making grooves, necessary beading, making edges, skirting etc, including making doors with all Hettich or equivalent accessories and door frame in necessary wooden section, polishing etc. complete | 100 | SqM
14 | PARITION IN ACP PANEL Providing and fixing partitions in 4 MM ACP panel both side laminate with framing in aluminium pipe of 1" x 2" in vertical at 4' vertical intervals and 3' horizontal members, with as approved by architect including making grooves, necessary beading, making edges, skirting etc, including making doors in ACP panel with all Hettich or equivalent accessories and door frame in necessary aluminium section etc. complete | 50 | SqM
15 | SOLAR SYSTEM Providing, supplying, installation and commissioning of appropriate design as approved by architect and engineer solar grid integrated system on roof top with solar PV module of ply crystalline silicon laminated with vacuum laminated glass of efficiency above 13% including mild steel module mounting structure (ms angle and ms flats) protected from corrosion with hot dip galvanized. Battery bank battery voltage 240 V DC of DOD allowed tubular battery 80% max, with efficiency 85%, capacity 240 V 350 Ah, tubular lead acid flooded electrolyte. Invertor of efficiency 90% +, solar charge controller, copper cables, all cables, MCB and accessories for integration with DG set and electric panel, etc. complete. Contractor to provide all design details in tender. | 0 | No.s
16 | REPAIR OF CONCRETE Providing and applying polymer modified plaster of 20 mm thick in C.M. 1:3 and adding polymer such as Webercrete, Roff Supercrete, Monobond, Perma Shield, Hypercrate, Dr. Fixit Powercrete at 6.00 litres in 1 bag of Cement and polyprolen fibers @125 gm Polymer powder superscreed or equivalent @ 3.3 kg/ per bag of cement and Superscreed P @ 1 bag per bag of cemeny to damaged structural concrete members by removing chipping out loose concrete, cleaning surface by wire, etc. including curing with covering guarantee etc. complete. | 250 | SqM
17 | WATER PROOFING TO WALL SURFACE Providing and applying water proofing treatment to vertical surface of basement and other walls, in all directions by using standard acrylic copolymer coating of Roff Hyguard, Monopoly 456, Dr. Fixit Pidilite 2K or equivalent in two coats including cleaning the surface by wire brush, washing and drying including covering guarantee of 10 years and as directed by Engineer In Charge etc. complete. |  | SqM
18 | LIGHTING ARESSTERS
A | Lightning arrestor station type 11KV grade | 4 | No.s
B | supplying and erecting earth pit of minimum bore dia. 150mm size, approved make Safe Earthing Electrode consisting Pipe-in-Pipe technology as per IS 3043-1987 made of corrosion free G.I. Pipes with constant ohmic value surrounded by highly conductive compound with high charge dissipation suitable for effective and maintenance free earthing as mentioned below :With 3 mtr. G.I. Pipes having outer pipe dia of 50mm having 80-200 micron galvanizing, Inner pipe dia. of 25mm having 200250 Micron galvanizing, connection terminal dia.of 12mm in nominal soil with 50 kg (Two Bag) Back filling Compound. | 4 | No.s
C | Covered copper wire (3 X 6 sq. mm) | 100 | Rmt
19 | PASSANGER LIFTS Proviiding and fixing passenger lifts in the hostel blocks with 12 persons capacity with approved speed as per the site conditions with grills gates, automatic breaking, electric panels etc. complete | 5 | No.s
20 | RO SYSTEN Providing and fixing RO system for the hostels with three levels filtration system to allow with approved make and model etc. complete | 4 | No.s
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## ABS GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
ABSTRACT BILL OF QUANTITIES
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
S/N | DISCRIPTION |  |  |  | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | THIRD FLOOR
2 | FOURTH FLOOR
3 | TERRACE FLOOR
4 | SANITATION WORKS
5 | ELECTRICAL WORKS
6 | CCTV SYSTEM
7 | MISCELLENIOUS
8 | SUB TOTAL
9 | TOTAL | [5 empty] | 0
|  | Conversion Rate: | 65.33 | USD |  | Dt.: 13-11-2017

## 3F GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ FOR THIRD FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING FLOORING AND PAVING Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 365.4798 | CuM
2 | DISMANTLING CONCRETE MEMBERS SLAB, STAIRCASE, BEAMS, COLUMNS OR WALLS Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 55 | CuM
3 | DISMANTLING LANDSCAPE WORK Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 110 | Cum
4 | DISMANTLING BRICK WALLS Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 150 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 560.4798 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 5326.62 | SqM
7 | REMOVING OLD PAINT AND MAKING SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 1328.5334 | SqM
8 | Providing and laying in position cement concrete in RCC columns for reinforced cement concrete work, using cement content as per approved design mix etc. complete. | 146.7906 | CuM
9 | Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 21.896 | CuM
10 | Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 15.4 | CuM
11 | Centering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 453.786 | SqM
12 | Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 12886.062 | Kg
13 | Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineer-in-Charge. (The payment of RCC band and reinforcement shall be made for separately). | 815.7444 | CuM
14 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 81.5744 | SqM
15 | INTERNAL PLASTER FOR REPAIR OF SPALLING IN SLABS, BEAMS AND COLUMNS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 1328.5334 | SqM
16 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 0 | SqM
17 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 250.8 | SqM
18 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 509.6646 | SqM
19 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 411.2237 | SqM
| SIZE: 800 X 800 (Avg.) | 164.4895 | SqM
| SIZE: 600 X 1200 (Avg.) | 164.4895 | SqM
20 | MS FABRICATION WORK FOR REPAIR, JACKETING STRUCTURAL MEMBERS ETC. Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 265.7067 | SqM
21 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws(including necessary handles, knobs, locks, tower bolt stopper etc. complete | 453.6 | SqM
22 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm | 422.94 | CuM
23 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 1328.5334 | SqM
24 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 0 | SqM
25 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. | 80 | No.s
26 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete
|  | 80 | No.s
27 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Conf. Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). | 10
28 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 50 | SqM
29 | MODULAR KITCHEN PLATFORM FOR PANTRY Providing and fixing Modular kitchen as per drawings with polished Stainless Steel platform with large size Stainless Steel wash basin with S trap and cleaning Jali. Modular kitchen will be made form 18 mm thick marine ply with glazed finished laminates of white and black colors with Hettich fittings of auto swing/close type. Internal wet and dry arrangement shall be made with use of Stainless Steel trays with all system for crockery, utensils, spoons, knifes etc. complete. Framing of the modular kitchen shall be in MS pipes with pure polyester coating from inside and outside. Powered coating shall be provided above pure polyester coat of approved quality, color, micron etc. complete. Kota stone base shall be provided to the SS platform. Proper slope for drain in Platform and floor shall be provided with Nahani trap. Electrical points at suitable locations shall be provided at suitable locations. | 0 | No
Additional glass cookery cabinet on wall above platform of approved quality and as per design shall be provided. electronic exhaust chimney of approved make shall be provided by the contractor. Any additional requirements shall be clarified before quoting for this item.
30 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | No.s
31 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 25 | No.s
32 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 4 | No.s
33 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 4 | No.s
34 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 4 | No.s
35 | POWDER COATED ALLUMINUM LOUVERED WINDOWS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 17.28 | SqM
36 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 4.968 | Nos
37 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. | 50 | SqM
38 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete | 50 | SqM
39 | REPAIR OF ENTRANCE PORTCH Repair of entrance porch by water proofing in bitumen with tile finish on top surface (as per water proofing specifications), replacement of old drainage with new drainage system, including painting, re concreting the floor etc. complete | 4 | No.s
40 | PANTRY PLATFORM Providing and fixing pantry platform in traditional Indian design in front of auditorium entry as approved by architect or engineer in Corian and MR 18mm play with internal lighting, glass work etc. complete | 4 | No.s
41 | CABINATE IN PANTRY Providing and fixing 3.2 m (l) x 0.45 (w) x 3.0 (h) cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 4 | No.s
42 | EXTERIOR CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. | 150 | SqM
43 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 250 | SqM
44 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete | 250 | SqM
TOTAL

## 4F GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ FOR FOURTH FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING FLOORING AND PAVING Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 365.4798 | CuM
2 | DISMANTLING CONCRETE MEMBERS SLAB, STAIRCASE, BEAMS, COLUMNS OR WALLS Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 55 | CuM
3 | DISMANTLING LANDSCAPE WORK Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 110 | Cum
4 | DISMANTLING BRICK WALLS Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 30 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 560.4798 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 5326.62 | SqM
7 | REMOVING OLD PAINT AND MAKING SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 1328.5334 | CuM
8 | Providing and laying in position cement concrete in RCC columns for reinforced cement concrete work, using cement content as per approved design mix etc. complete. | 146.7906 | CuM
9 | Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 20.621 | CuM
10 | Providing and laying in position cement concrete in RCC waist slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 18.48 | CuM
11 | Centering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 454.3275 | SqM
12 | Providing and fixing in position of M.S./HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 13012.412 | Kg
13 | Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineer-in-Charge. (The payment of RCC band and reinforcement shall be made for separately). | 1088.5141 | CuM
14 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 108.8514 | SqM
15 | INTERNAL PLASTER FOR REPAIR OF SPALLING IN SLABS, BEAMS AND COLUMNS Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 1328.5334 | SqM
16 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 0 | SqM
17 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 2471.9703 | SqM
18 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 741.5911 | SqM
19 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 513.613 | SqM
| SIZE: 800 X 800 (Avg.) | 205.4452 | SqM
| SIZE: 600 X 1200 (Avg.) | 205.4452 | SqM
20 | MS FABRICATION WORK FOR REPAIR, JACKETING STRUCTURAL MEMBERS ETC. Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 265.7067 | SqM
21 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws(including necessary handles, knobs, locks, tower bolt stopper etc. complete | 593.46 | SqM
22 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm | 553.21 | CuM
23 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 1328.5334 | SqM
24 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 0 | SqM
25 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. | 112 | No.s
26 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete
|  | 112 | No.s
27 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Conf. Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). | 112 | No.s
28 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 50 | SqM
29 | MODULAR KITCHEN PLATFORM FOR PANTRY Providing and fixing Modular kitchen as per drawings with polished Stainless Steel platform with large size Stainless Steel wash basin with S trap and cleaning Jali. Modular kitchen will be made form 18 mm thick marine ply with glazed finished laminates of white and black colors with Hettich fittings of auto swing/close type. Internal wet and dry arrangement shall be made with use of Stainless Steel trays with all system for crockery, utensils, spoons, knifes etc. complete. Framing of the modular kitchen shall be in MS pipes with pure polyester coating from inside and outside. Powered coating shall be provided above pure polyester coat of approved quality, color, micron etc. complete. Kota stone base shall be provided to the SS platform. Proper slope for drain in Platform and floor shall be provided with Nahani trap. Electrical points at suitable locations shall be provided at suitable locations. | 0 | No
Additional glass cookery cabinet on wall above platform of approved quality and as per design shall be provided. electronic exhaust chimney of approved make shall be provided by the contractor. Any additional requirements shall be clarified before quoting for this item.
30 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | No.s
31 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 25 | No.s
32 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 4 | No.s
33 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 4 | No.s
34 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 4 | No.s
35 | POWDER COATED ALLUMINUM LOUVERED WINDOWS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 21.168 | SqM
36 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 5.832 | Nos
37 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. | 50 | SqM
38 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete | 50 | SqM
39 | REPAIR OF ENTRANCE PORTCH Repair of entrance porch by water proofing in bitumen with tile finish on top surface (as per water proofing specifications), replacement of old drainage with new drainage system, including painting, re concreting the floor etc. complete | 4 | No.s
40 | PANTRY PLATFORM Providing and fixing pantry platform in traditional Indian design in front of auditorium entry as approved by architect or engineer in Corian and MR 18mm play with internal lighting, glass work etc. complete | 4 | No.s
41 | CABINATE IN PANTRY Providing and fixing 3.2 m (l) x 0.45 (w) x 3.0 (h) cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 4 | No.s
42 | EXTERIOR CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. | 150 | SqM
43 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 250 | SqM
44 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete | 250 | SqM
TOTAL

## TRF GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ FOR TERRACE FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 2135.04 | CuM
2 | ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 151.2 | SqM
3 | BRICK WORK Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 45 | CuM
4 | WATER PROOF CEMENT PAINT Providing and applying two coats of waterproof cement paint of an approved make and colour as per manufacturers specifications to smooth sand faced or other surfaces, upto 10m height from ground level and at all locations as directed including preparing surfaces for painting by any approved means, watering, scaffolding, cleaning and curing etc. complete as directed by Engineer-in-charge. | 40.7818 | SqM
5 | UPVC PIPES AND BENDS Providing and fixing UV resistant self fit UPVC pipes of approved make for Rainwater down takes confirming to IS 13592:1992 Type A suitable for 4kg/sqcm pressure for following pipe diameters including rain water receiving recess with pvc plug bend necessary fittings such as offsets shoes, fixing the pipes on wall with clips filling the joints with solvent/cement and necessary scaffolding etc. complete as directed by Engineer In Charge. 150mm dia | 150 | Rmt
6 | WATER PROOFING TO TERRACE Providing water proofing treatment of Old Terraces by removing existing treatment. Sealing of cracks by non shrink cracks fill compound by applying first coat of polymer modified semi-viscous paste prepared by mixing polymer of approved make (such as Aquatek conchem/ Master Seal 550/brush bond / RoffSupercrete/ Webercrete/ Monobond / Perma shield / Hypercrate / Master Crete M 81/ MC-Bauchemie) and Cement in 1:2proportion ( 1 litre polymer : 2 Kg Cement) or Rohnex water proofing system in two coats(1kg powder,700 ml water and polymer jelly for first coat & 1 kg powder,500 ml water & polymer jelly for second coat) to a neatly cleaned and dust free concrete surface and upto 300 mm over parapet wall prepared by removing loose and deposited material with brush and water, laying glass fibre mesh of 10 x 10 specification of approved make over tacky surface of first coat of polymer followed by second coat in transverse direction, laying mechanical protective cover to polymer coating treatment with brick bat coba with burnt broken brick bats laid in C.M. 1:5 admixed with approved water proofing compound, filling up to half depth of brick bats, curing this layer for 3 days, | 31.3706 | Sq.M
applying cement slurry over this layer joints of brick bats with C.M. 1:3 admixed making the Sq.m. 1102.00 219.00 junctions at the parapet rounded and tapered top for required height, with drip mould at the junction of plaster and parapet and curing and covering 7 years Guarantee against leak proofness on court including ponding test etc. complete (Make: Dr. Fixit Roofseal or equivalent)
7 | GROUTING TO VARIOUS PARTS Providing Grouting by specially prepared grout of Weber Crete /Roff Supercrete /Polyalk P/Monobond /Perma shield/Hypercrate or equivalent with cement in proportion 1:3.5 (1 part chemical & 3.5 part cement by weight) along with 50 ml super plasticizer Roff Plast 320/sun polycrete NCT/Perma Plast/Supercon 100 or non shrinking, non cracking antiwash high strength polymer cement grout P C grout available in bags or equivalent with proper water for injectable consistency and applying it in the body of structure like slab, beam, column, pillars, deckslab, retaining wall, basement, underground and elevated water storage reservoir concrete and brick wall, crack portion of structure etc. by injectng method, to achieve its original strength including drilling of suitable diameter drills holes at 2 to 4 Nos. per sqm. using caps and nozzle grouting machinery necessary, scaffolding, finishing and covering gurantee of 10 years and necessary testing etc. complete. | 250 | Kg
8 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 250 | SqM
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## SAN GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ FOR SANITATION WORK FOR ALL FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | WHITE COLOR WATER CLOSET Providing & Fixing star white color vitreous China wall mounted water closet with heavy duty soft close seat cover & concealed dual tank. Complete with all accessories like pipes, cistern etc. including cutting & making good wall & floor wherever required. (Model PERRYWARE PETIT S OR Equivalent Standards Dimension: 380*360*545 or more) | 38 | No
2 | WHITE COLOR WASH BASIN OVAL SHAPE Providing & Fixing star white color vitreous China wash basin Oval shape, 32mm dia C.P waste, 32mm Dia C.P wall flange & rubber adopter for waste connection complete, including cutting & making good the walls wherever required. (Model - Perryware Cascase NXT BC Basin or Equivalent Dimension: 555 x 450 x 205 or more) Note: Contractor shall approve the make and design from Engineer Incharge. | 15 | No
3 | WHITE COLOR URINAL Providing & Fixing star white color vitreous China urinal with inbuilt auto flush system with s.s. bracket, pipe to wall with C.P flange compete including cutting & making good the walls & floors wherever required. Model Perryware New Magnum Standard Urinal, or Equivalent, Dimension: 380*400*590 or more) Note: Contractor shall approve the make and design from Engineer Incharge. | 9 | No
4 | STAINLESS STEEL SINK Providing & Fixing in position best stainless steel sinks with 40mm C.P. brass waste chrome plated & s.s. waste pipe. complete in all respect including cutting & making good the walls & floors. in canteen. Jaguar/Sunfold/Equivalent 24"X20"X8" 1.0mm thick mat finish. Note: Contractor shall approve the make and design from Engineer Incharge Embassy | 2 | No
5 | WALL MOUNTED TAP Providing & Fixing chrome plated wall mounted taps over wash basin complete in all respect including cutting & making good the walls wherever required (Make: As approved by the Engineer Incharge) | 21 | No
6 | STOP TAP FOR WATER CLOSET Providing & Fixing 15mm C.P brass bib tap for water closet with C.P brass threaded flange complete, including cutting & making good the walls wherever required. Model - : Contractor shall approve the make and model form Engineer Incharge | 38 | No
7 | ANGLE VALVE FOR WATER CLOSET Providing & Fixing 15mm C.P. brass angle valve with C.P copper connecting pipe 375mm long & nuts, washer & C.P. brass flange complete, including cutting & making good the wall wherever required. JAQUAR CONTINENTAL 053 KN for water closet cistern & basins. or Equivalent in Kohler/TOTO/American Standards | 38 | No
8 | STOP COCK FOR URINAL BEFORE SENSOR Providing & Fixing concealed stop cocks for cold water supply. Note: Contractor shall approve the make and design from Engineer Incharge Embassy | 38 | No
9 | BRASS MIXING FITTING FOR SINK Providing & Fixing 15mm C.P. brass mixing fitting for sink with swinging spout complete, including cutting & making good the walls wherever required. Wall mixer with swivel spout. Note: Contractor shall approve the make and design from Engineer Incharge Embassy | 38 | No
10 | AUTOMATIC SOAP DISPENSER Providing & Fixing ABS body automatic liquid soap dispenser for all was basins with liquid soaps. Note: Contractor shall approve the make and model from Engineer Incharge Embassy) | 17 | No
11 | CROMIUM PLATED TOWEL ROD 16 MM DIA Providing and fixing chromium plated towel rod 16 mm dia. and 75 cm. in length including all accessories, fitting, cleaning, etc. complete. | 14 | No
12 | PVC NAHANI TRAP Providing and fixing 150 cm Rigid PVC Nahani Trap including PVC grating, bend, connecting piece of P.V.C.pipe of required diameter, pipe up to the outside face of the wall, making good the holes and repairs, testing, including cover etc. complete. | 40 | No
13 | MIRROR IN TOILET Providing and fixing 2000 mm x 900 mm size superior type mirror with 16 mm dia including chromium plated towel rod etc. complete. Note: Contractor shall approve a sample from architect/engineer incharge | 38 | No
14 | PIPE FOR DRAINAGE Providing and fixing in position Heavy type alkathene pipe for drainage connections including cutting, boring holes in wood work or masonry if necessary, making connections of pipe to sink and giving test for no leakages, making good the damaged surface etc. complete. As directed by Engineer in-charge
| 25 MM Dia | 3000 | Rmt
| 40 MM Dia | 2500 | Rmt
15 | PIPE FOR RAINWATER DRAINAGE Providing and fixing in position Heavy type alkathene pipe for drainage connections including cutting, boring holes in wood work or masonry if necessary, making connections of pipe to sink and giving test for no leakages, making good the damaged surface etc. complete. As directed by Engineer in-charge Embassy.
| 250 MM Dia | 750 | Rmt
16 | UPVC WASTE PIPE Providing and fixing UPVC waste pipes for Wash Basin / Urinals including all fittings, making chases in wall / floor and reinstating the surface. etc. complete. As directed by Engineer in-charge Embassy.
| 50 mm Dia | 750 | Rmt
| 40 MM Dia | 1500 | Rmt
17 | PVC PIPE Providing, cutting, erecting, jointing, clamping, fixing including making clamping, fixing including making opening in walls, floors, S.W.R., P.V.C. pipe and fittings, such bends, elbows single junction, double junctions, cowls with PVC / G.I. brackets etc. including jointing with solvent cement/rubber ring, making necessary holes in masonry / concrete, all installation as workmanship like manner and as per manufacturer's instructions, testing, commissioning the lines, attending to leakage if any making it to good leakage if any making it to good condition. Following diameters of S.W.R.PVC pipe and fittings of approved make conforming to IS 13592-1992. All as directed.
| 110 mm. dia. PVC pipe for soil stack | 350 | Rmt
| 75 mm. dia. PVC pipe for waste wear pipe | 250 | Rmt
| 50 mm. dia. PVC pipe for anti-symphonic pipe | 75 | Rmt
18 | RECTANGULER TISSUE PAPER HOLDER FOR LADIES AND GENT TOILET Providing and fixing rectangular tissue paper holder in ladies and gents toilet for holding hand wash tissue papers, with additional storage facilities etc. complete (Model: As approved by Engineer Incharge) | 38 | No
19 | TOILET TISSUE PAPER HOLDER Providing and fixing toilet tissue paper holder in ladies and gents toilet for holding hand wash tissue papers, with additional storage facilities etc. complete (Model: As approved by Engineer Incharge) | 38 | No
20 | WATER TANK Providing and fixing PVC tank of appropriate capacity in basement, roof and other places etc. complete | 15000 | Ltrs
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## ELE GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ FOR ELECTRICAL WORK FOR ALL FLOORS
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | POINT WIRING FOR INDEPENDENT PLUG Providing, fixing and testing point wiring for independent plug in 20 mm rigid PVC conduit with 1.5 sqm FRLS grade Copper wire with modular switch and concealed wiring with necessary joints, and required accessories complete. As directed by Engineer in-charge | 430 | No.s
2 | LIGHT POINT WITH SINGLE MODULER SWITCH Providing, fixing and testing light point with single modular switch with concealed cables and modular plate etc. complete. | 467 | No.s
3 | POINT WIRING FOR WALL MOUNTED FANS Providing, fixing and testing point wiring for wall mounted fans in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade Copper wire with flush type switch and required accessories etc. complete. | 253 | No.s
4 | CEILING FANS Providing, supplying and fixing ceiling fans of with regulator and all other accessories, etc. complete (Make: Bajaj or equivalent) | 104 | No.s
5 | LED BATTEN LIGHTS Supply, Installation, testing & commissioning of the 36 watt or above, concealed LED circular light fixture in console room complete with copper choke, starter, LED etc. (Make PHILIPS Mirolta Pro r16 36 Watts LED Batten - High Power High Performance Tube Light - Cool Day Light or equivalent) | 154 | No.s
6 | CEILING CIRCULER LIGHT PANEL Supply, installation, testing & commissioning of white color ceiling fixture of material metal and glass with 15 watt or above LED light including, started, LED system, switches etc, complete (Make: Philips myLiving canvas white model no. 77050/31/16 or equivalent) | 50 | No.s
7 | STEPS AND RAMP LIGHTING Supply, Installation, testing & commissioning for steps in auditorium, steps, below seats and ramp lighting of the watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania: wall 5 STE DIR 4W LED WHT LLB with switches etc. | 150 | Rmt
8 | PENDENT LIGHT IN LOBBY Providing, installation, testing & commissioning of 6-1/2’’ Pendalyte with Satined Aluminium Reflector, with suspended, lamp holder, LED/CFL lamp of 32 watt and above etc. complete (Make: Philips Pendalyte with Satined Aluminium Reflector or equivalent) | 10 | No.s
9 | HANGING LIGHT FIXTURES FIXTURE Supply, Installation, testing & commissioning hanging light fixtures in lotus shape made from brass of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested
| Large | 5 | No.s
| Small | 5 | No.s
10 | WALL LED LIGHT Providing, supplying, installation as commissioning, regular 26 watt and above light fixtures with light holder of approved quality including concealed cabling, modular switch, texted as approved by engineer, with wiring, scaffolding, etc. complete (PHILIPS 26-watt LED Bulb ¦AceBright High Wattage LED Bulb Base: B22 Light Bulb for Home ¦ Crystal White or equivalent) | 25 | No.s
11 | WALL MOUNTED FIXTURE Supply, Installation, testing & commissioning for curved wall in console room of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested | 10 | No.s
12 | LED TUBE ON TERRACE Supply, installation, testing and commission of LED tube25 watt or above of material glass and plastic including bulb, clips, LED system, civil work etc complete(Make: Philips Linea 26-Watt LED Tube (White) or equivalent) | 10 | No.s
13 | LED STRIP LIGHTS Supply, installation, testing and commissioning of LED strip lights 8 watt above per metre of required color or hue including, adaptor, controller, male-female clips, cable, switches etc. complete in ceiling, tables, with scaffolding, glass etc. complete. (Make: Philips 800284 Hue Light strip Plus, 2Nd Generation or equivalent) | 50 | No.s
14 | EXTERIOR LED LIGHTS FOR BUILDING Supply, Installation, testing & commissioning for lights in exterior in elevation of LED or compliance concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. Contractor shall assign specialised company for design and installation of external lighting with previous experience in similar field. Contractor and subcontractor shall approve the design for external lighting from architect or engineer any suggestions shall be incorporated with all necessary requirement etc. complete This item include AMC for three years.. | 1 | No.s
15 | POINT WIRING FOR LAN POINTS Point wiring for LAN points will be carried out with CAT 6, LAN Cable, in surface/ recessed existing PVC conduits, inclusive of p/f of G.I/ PVC box & modular plate RJ 45 AT&T LAN socket. Work includes cutting & repair of chase to original finish. (Make of cable: Polycap or equivalent) | 50 | No.s
16 | CIRCUIT WIRING Supply and wiring wall / floor etc. / recessed / surface as per colour code with the following size PVC Insulated copper wire along with given earth wire for phase neutral and earth conductor with standard colour coding, through ISI marked rigid PVC conduit of given size with all accessories. The rate includes the cost of complete wiring from switch box to switch box etc. complete (Make of wire: Polycap or equivalent)
a. | 2 x 1.0 Sqmm PVC Copper wire in 20 mm dia conduit for Emergency Stop Box Connection | 1500 | Rmt
b. | 3 x 1.5 Sqmm PVC Copper wire with in 20 mm dia conduit (The rate includes the cost of complete wiring between individual switch boards) | 1500 | Rmt
c. | 3 x 2.5 Sqmm PVC Copper wire with in 20 mm dia conduit (for lighting main circuit, 15A plug points & UPS point wiring & 1T AC) | 1500 | Rmt
d. | 5 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 3-Ph circuits like 3-Ph AC / UPS) | 1500 | Rmt
e. | 3 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 1.5/2Tonne AC and UPS I/P & O/P upto UPS O/P DB and for Sign Boards if there are multiple Name boards) | 800 | Rmt
17 | AC/HEATER METAL BOX Supplying and fixing for AC/Heater metal box of GI box with modular plate and cover in front on surface or in recess , including providing and fixing of 3 No's 3 pin 5/6 amps modular socket outlet and 15/16 amps. Modular switch, connections, painting etc. as required | 154 | No.s
18 | TWO WAY CONNECTIONS Point wiring for two way connects for switching lights in corridor, toilet, landscape, steps in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade copper wire with flush type switch and required accessories. | 50 | No.s
19 | UTP NETWORK CABLE CAT 6 Supplying & installing UTP networking Cat-6+ cable suitable for LAN / WAN Computer networking. | 50 | No.s
20 | M. S. CABLE TRAY Fabrication and installing required sizes of perforated M.S. cable trays including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with M.S. suspenders and including painting with powder coating etc. as required. | 1 | No.s
21 | DISTRUBUTION BOARD Distribution board of approved make as per design requirements of Legrand or equivalent make with MCB cables, separation for computers, lights etc. complete | 8 | No.s
22 | PVC CABLE Supply and erecting PVC armoured cable 2 core 2.5 sq. mm stranded/solid copper conductors continuous 5.48 sq. mm (12 swg) GI earth wire complete erecting with glands & lugs on wall in trenches complete (Measurement to be as per site condition and location of Mains) (Make: Polycap or equivalent) | 1500 | Rmt
23 | SUPPLY 16" EXHAUST FAN Supply of 16" exhaust fan of PVC of high speed with installation, testing including aluminium or wooden framing etc. complete. (Make Godrej/Philips or equivalent) Note: Contractor shall approve the make and model from Engineer in-charge of Embassy) | 32 | No.s
24 | BELL POINTS Providing and fixing bell points with concealed conduits with cable, bell of approved make, modular switches, etc. complete | 6 | No.s
25 | TELEPHONE POINTS Providing and fixing telephone points with modular plate, cable, switch with concealed cabling etc. complete | 20 | No.s
26 | EARTHLING WITH G.I. EARTH PIPE Earthling with G.I. earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but without charcoal or coke and salt) as required. | 25 | No.s
27 | MUSIC CUM PA SYSTEM OF PHILIPS MAKE Providing and fixing music systems of Philips make with speakers, CD, USB, Radio etc. complete as approved by engineer incharge with stereo speakers in appropriate locations, including stereo head phones etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. Design & product detail to be submitted with tender. | 4 | No.s
28 | MODULAR KITCHEN HOT PLATE Providing and fixing modular kitchen hot plate with 4 no. of coils of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. | 4 | No.s
29 | MODULAR KITCHEN GRILL AND OVEN Providing and fixing modular kitchen grill and oven of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. | 4 | No.s
30 | MODULAR KITCHEN FRIDGE Providing and fixing modular kitchen fridge of approved size and capacity Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer incharge Embassy. | 4 | No.s
31 | WATER HEATER Supplying, installation, and testing Smith-Jaguar water heater with all accessories in Male and Female toilets complete. (Make: Jaguar CEWHR-DIGITAL Digital with remote & dual heating elements 35 19.00 395X760 1 KW/ 1.5 KW/ 2.5 KW) | 12 | No.s
32 | ELECTRICAL PANEL Suppling, installation, commissioning of main electrical panel in basement for all electrical equipments with all necessary requirements as approved by architect or engineer etc. complete. | 4 | No.s
33 | LANDSCAPE LIGHTS Providing and fixing landscape lights with fixture of approved make and models as per the design with weather protection of Philips or equivalent make with connections, installation etc. complete | 20 | No.s
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## CCTV GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ FOR CCTV SYSTEM
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DOME CAMERAS Supply Installation ,Testing & Commissioning for cctv Camera, Specification: High Resolution Digital Image Sensor HIKVISION 5 MP Indoor Dome CCTV Camera with inbuilt Audio Mic DS-2CE76H0T-ITPFS + USEWELL BNC/DC, White Wired, 1080P Image Sensor (Make: HIKVISION or Equivalent) | 20 | No.s
2 | BULLET CAMERAS Supply Installation Testing & Commissioning for cctv camera, Specification: HIKVISION 2MP Eco HD 1080P Night Vision Bullet Outdoor Wired CCTV Camera for 2MP & Above DVRs, White (Model: Hikvision or Equivalent) | 4 | No.s
3 | PTZ CAMERAS Supply installation and commissioning of CCTV camera etc. complete ( Make: HIKVISION 2-inch 4 MP Color Mini PT Dome Network Camera DS-2DE2C400SCG-E Compatible with JK Vision BNCor Equivalent) | 1 | No.s
4 | CONNECTOR FOR CCTV CAMERAS Connector for cctv camera, adaptor, | 25 | No.s
5 | NETWORK VIDEO RECORDER Supply, installation and commissioning of NVR:64 Channel 4K NVR, Plug And Play Black, Up to 8 SATA interfaces Third-party network cameras supported Up to 12 Megapixels resolution recording Support various VCA detection alarm and VCA search Support HDD hot swap with RAID0,1,5,6,10 storage scheme configurable etc. complete (Make: Hikvision DS-9664NI-I8 or equivalent) | 4 | No.s
6 | CAT 6 CABLE Cat 6 Cable including making hole, taking though ceiling though pipe, concealing, scaffolding etc. complete | 900 | No.s
7 | JOYSTICKS FOR CCTV CAMERAS CCTV LCD Screen Display joystick keyboard controller for PTZ Cam Camera, LCD display In-built multi-protocol maximum controllable 128 units PTZ camera 2D joystick controller etc. complete (Make: Sony or equivalent) | 1 | No.s
8 | LED TV 65 INCH Sony XBR-65X850E 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) w/ 3 Month Netflix Subscription, Sony AUTHORIZED DEALER - Includes Full Sony USA WARRANTY Sony 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) Go beyond what you've seen before with remarkable 4K HDR clarity, color and contrast. Scenes are more detailed, more natural and more real with 4K HDR Processor X1, and life's brilliance is revealed with extra smooth and vibrant colors INCLUDED IN THE BOX: Sony 65" Class (64.5" Diag.) LED 2160p Smart 4K Ultra HD TV with High Dynamic Range - AC power cord - Batteries - IR blaster - Owner's manual - Table top stand (separate, assembly required) - Voice remote control (RMF-TX300U) BUNDLE INCLUDES: Sony XBR-65X850E 65-inch 4K HDR Ultra HD Smart LED TV (2017 Model) | 1 | No.s
9 | RACK Supply, installation and fixing Wall Mount Network Server 19 Inch IT Cabinet Rack Enclosure Glass Door Lock, Dimensions: 20"H x 23.5"W x 18"D 130 pound weight capacity Included ground wire Fits Standard 19" rack-mount equipment Total Usable Space of 16" front to back (Make: NavePoint 9U or equivalent) | 1 | No.s
10 | Installation of various items and deviation items for complete work | 1 | No.s
11 | AMC Annual Maintenance Comprehensive | 1 | No.s
Total

## MISCELL GH
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: GIRLS HOSTEL AND FACULTY BLOCKS (BLOCK 1, 2, 3 AND 4)
BOQ OF SIGNAGES AND MISCELLANEOUS ITEMS
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | LARGE LETTERS Providing and fixing Polish Stainless steel letter of Large Size (10" Height or of Size to be approved from Engineer Incharge) in Polish Stainless Steel of high grade that will not corrode in the environment of refinery. Light shall be long life and easy to maintain preferable of brands Philips or equivalent | 10 | No.s
2 | SMALL LETTER SIGNAGES Providing and fixing office signage at to of cabins, and all other rooms in polish stainless steel with letter size (1" or as advised) and design approved by the engineer incharge etc. complete | 20 | No.s
3 | NATURAL PLANTERS WITH CONCRETE POTS Providing and fixing natural planter out side building on 750 Dia on top of concrete pot of approved design by the engineer incharge, including full grown plant as approved by client etc. complete | 10 | No.s
4 | ARTIFICIAL PLANTERS WITH CERAMIC POTS Providing and fixing artificial planter with ceramic pot, white stone as approved by the engineer incharge | 15 | No.s
5 | WALL PAINTINGS Providing and fixing wall painting of approved make in various room with proper hanging arrangement in wall etc. complete | 10 | No.s
6 | LOCKER IN TOILETS Providing and fixing lockers in ladies toilet in Stainless Steel of minimum 8 nos and type of Godrej or Equivalent make etc. complete | 20 | No.s
7 | FIRE FIGHTING SYSTEM Providing and fixing proposed fire fighting system as per drawing as approved by architect or engineer including all necessary requirements for electrical, safety, approvals from local fire department etc. complete |  | No.s
| 1) Wet Sprinklers System | 1 | No.s
| 2) Dry Sprinklers System | 1 | No.s
| 3) Fire Hose Piping | 1 | No.s
| 4) Fire Alarm System | 1 | No.s
| 5) Fire Signage, Escape Routes etc. | 1 | No.s
8 | FOAM EXTINGUISHER Making and fixing concealed cabinets for fire / foam extinguisher at appropriate location with fire signage in a) Console room entry in ACP wall panels, b) Console Room curved partition, c) office corridor, d) Kitchen and Pantry, and d) Toilets or at locations as advised. | 0 | No.s
9 | TEMPARARY ELECTRICAL CONNECTION Providing and fixing permanent electric connection to building from local electrical office including cabling, sub meters, including preparation of load sheets, drawings etc. complete | 1 | No.s
10 | DIESEL GENERATOR SET Design, manufacture, supply at site, storing, handling, installation, testing and commissioning of following sizes of DG sets in sound proof enclosure (to meet the requirements of central pollution control board) as per specification complete in all respect 415Volts, 3 phase, 50 Hz, 1500 RPM AC alternator coupled to diesel engine complete with all accessories as per specifications tool kits, service manual, self starting device, fly wheel, coupling with guard, V belt, radiator cooling system, instrument panel, common bed plate, anti vibration isolation pads, grouting bolts, XLPE/PVC armoured cables and terminal box as per specification, adopter box, glands, nuts etc. first filling of Engine oil, Gear oil, high speed diesel oil, 24 volts chargeable battery set (Minimum 180 AH capacity) complete with batteries, battery charger etc. DG set including exhaust system, copper flexible expansion joints, silencer, fuel oil day tank, fuel oil piping, oil hand pump, steel support structure, logic panel (weather proof) with AMF operation, civil work etc. complete. |  | No.s
11 | It shall be salient with international noise international emission norms. It shall be compatible for basement as per norms. Any civil work for or necessary requirements shall be considered for basement installation. DG set include automatic switch during the power cuts. (Cummins/Kirloskar/ Volvo or Equivalent) |  | No.s
| 225 KVA | 0 | No.s
| 180 KVA | 0 | No.s
No.s
12 | METAL RATED FIRE DOORS Manufacturing, supplying, installation of metal fire door of approved color and make with door frame of material galvanized steel 2mm, of size standard Heights ( Wall Openings) 2100 mm with ador leaf in galvanized steel 1.6 mm thick, Infill with Rockwool thickness 45 mm, width 1200, fire Rating of120 Mins, hardware (all hardware parts are ISI marked), SS Hinges 4" x 12, SS D Handle 12", door Closer, dead lock with both side key, vision panel 300 x 300, fully flush construction with no visible welds, robust structure, ease of operation, maintenance-free & high level of aesthetic, including removal of existing doors, making surface good etc. complete | 2 | No.s
13 | PARITION IN 18 MM PLY Providing and fixing partitions in ant termite, moisture resistant ply with framing in aluminium pipe of 1" x 2" in vertical at 4' vertical intervals and 3' horizontal members, with 18 mm ply with 1 mm laminate (texture or glassy or plain) as approved by architect including making grooves, necessary beading, making edges, skirting etc, including making doors with all Hettich or equivalent accessories and door frame in necessary wooden section, polishing etc. complete | 100 | No.s
14 | PARITION IN ACP PANEL Providing and fixing partitions in 4 MM ACP panel both side laminate with framing in aluminium pipe of 1" x 2" in vertical at 4' vertical intervals and 3' horizontal members, with as approved by architect including making grooves, necessary beading, making edges, skirting etc, including making doors in ACP panel with all Hettich or equivalent accessories and door frame in necessary aluminium section etc. complete | 50 | No.s
15 | SOLAR SYSTEM Providing, supplying, installation and commissioning of appropriate design as approved by architect and engineer solar grid integrated system on roof top with solar PV module of ply crystalline silicon laminated with vacuum laminated glass of efficiency above 13% including mild steel module mounting structure (ms angle and ms flats) protected from corrosion with hot dip galvanized. Battery bank battery voltage 240 V DC of DOD allowed tubular battery 80% max, with efficiency 85%, capacity 240 V 350 Ah, tubular lead acid flooded electrolyte. Invertor of efficiency 90% +, solar charge controller, copper cables, all cables, MCB and accessories for integration with DG set and electric panel, etc. complete. Contractor to provide all design details in tender. | 0 | No.s
16 | REPAIR OF CONCRETE Providing and applying polymer modified plaster of 20 mm thick in C.M. 1:3 and adding polymer such as Webercrete, Roff Supercrete, Monobond, Perma Shield, Hypercrate, Dr. Fixit Powercrete at 6.00 litres in 1 bag of Cement and polyprolen fibers @125 gm Polymer powder superscreed or equivalent @ 3.3 kg/ per bag of cement and Superscreed P @ 1 bag per bag of cemeny to damaged structural concrete members by removing chipping out loose concrete, cleaning surface by wire, etc. including curing with covering guarantee etc. complete. | 250 | No.s
17 | WATER PROOFING TO WALL SURFACE Providing and applying water proofing treatment to vertical surface of basement and other walls, in all directions by using standard acrylic copolymer coating of Roff Hyguard, Monopoly 456, Dr. Fixit Pidilite 2K or equivalent in two coats including cleaning the surface by wire brush, washing and drying including covering guarantee of 10 years and as directed by Engineer In Charge etc. complete. |  | No.s
18 | LIGHTING ARESSTERS
A | Lightning arrestor station type 11KV grade
B | supplying and erecting earth pit of minimum bore dia. 150mm size, approved make Safe Earthing Electrode consisting Pipe-in-Pipe technology as per IS 3043-1987 made of corrosion free G.I. Pipes with constant ohmic value surrounded by highly conductive compound with high charge dissipation suitable for effective and maintenance free earthing as mentioned below :With 3 mtr. G.I. Pipes having outer pipe dia of 50mm having 80-200 micron galvanizing, Inner pipe dia. of 25mm having 200250 Micron galvanizing, connection terminal dia.of 12mm in nominal soil with 50 kg (Two Bag) Back filling Compound. | 4 | No.s
C | Covered copper wire (3 X 6 sq. mm) | 100 | Rmt
19 | PASSANGER LIFTS Proviiding and fixing passenger lifts in the hostel blocks with 12 persons capacity with approved speed as per the site conditions with grills gates, automatic breaking, electric panels etc. complete | 5 | No.s
20 | RO SYSTEN Providing and fixing RO system for the hostels with three levels filtration system to allow with approved make and model etc. complete | 4 | No.s
34 | LANDSCAPE WORKS Providing and supplying all the landscape work including paving, plants, lights, planters, construction in brick or concrete, approvals, detail design etc. complete | 0 | No.s
Total
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## ABS UT
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
ABSTRACT BILL OF QUANTITIES (BOQ)
NAME OF PROJECT: LECTURE HALLS IN UTILITY AND ACDEMIC BLOCKS AND RENOVATIONS OF LABORATORIES
S/N | DISCRIPTION |  |  |  | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | CIVIL AND INTERIOR WORKS
2 | TERRACE
3 | ELECTRICAL WORKS
4 | AIR CONDITIONING
5 | SUB TOTAL
6 | 5 % WATER SUPPLY & DRAINAGE
7 | 5 % FIRE FIGHTING SYSTEM
8 | TOTAL | [5 empty] | 0
|  | Conversion Rate: | 65.33 | USD |  | Dt.: 13-11-2017

## ALL LEVEL UT
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: LECTURE HALLS IN UTILITY AND ACDEMIC BLOCKS AND RENOVATIONS OF LABORATORIES
BOQ FOR CIVIL AND INTERIOR WORKS
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING FLOORING AND PAVING Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 264.075 | CuM
2 | DISMANTLING CONCRETE MEMBERS SLAB, STAIRCASE, BEAMS, COLUMNS OR WALLS Dismantling floor and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 82.5 | CuM
3 | DISMANTLING FALSE CEILING AND PARTITIONS WORK Dismantling false ceiling and partitions and taking away dismantled materials to necessary location as approved by owner. This include housekeeping for keeping area clean etc. complete | 110 | Cum
4 | DISMANTLING BRICK WALLS Dismantling brick work and taking away debris at necessary location. This include housekeeping for keeping area clean etc. complete | 150 | CuM
5 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 586.575 | CuM
6 | PRE-CONSTRUCTIONAL ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 853.6687 | SqM
7 | REMOVING OLD PAINT AND MAKING SURFACE Removing paint by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 341.25 | SqM
8 | RCC COLUMNS AND BEAMS Providing and laying in position cement concrete in RCC columns for reinforced cement concrete work, using cement content as per approved design mix etc. complete. | 25.668 | CuM
9 | RCC SLABS Providing and laying in position cement concrete in RCC slab for reinforced cement concrete work, using cement content as per approved design mix etc. complete | 58.6372 | CuM
10 | Centering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts etc. | 75 | SqM
11 | STEEL REINFROCEMENT Providing and fixing in position of HYSD bar reinforcement of various diameters for R.C.C. footing, foundations, slabs, beams and columns, chajjas, lintels etc. as per detailed design and drawings and schedules including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 5901.3633 | Kg
12 | CONCRETE HOLLOW BLOCK Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineer-in-Charge. (The payment of RCC band and reinforcement shall be made for separately). | 175.8844 | CuM
13 | BRICK WORK IN CEMENT MORTAR Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 52.7653 | SqM
14 | INTERNAL PLASTER Providing and applying 12 or necessary mm thick internal plaster in cement mortar 1:3 with at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding, coating reinforcement, chicken mesh etc. complete. | 1538.5435 | SqM
15 | MARBLE FLOORING Marble stone flooring with 18 mm thick Italian marble stone, as per sample of marble approved by Engineer-in-charge, over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with grey cement slurry, including rubbing and polishing and making floral pattern medallion and border, skirting, in flooring, staircase, including making patta, rounds edges, polishing edges as per design including polishing, cleaning etc. complete | 0 | SqM
16 | VITRIFIED TILES FLOORING Providing and laying Vitrified tiles in different sizes of double charge (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in flooring, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 250.8 | SqM
17 | VITRIFIED TILES SKIRTING Providing and laying Vitrified tiles in skirting of required sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 421.902 | SqM
18 | DIGITAL GLAZED VITRIFIED WALL TILES Providing and laying Digital Glazed Vitrified tiles in wall of required sizes (Matt/Glossy/Metallic) (thickness to be specified by manufacturer), with water absorption less than 0.08 % and on forming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.
| SIZE: 600 X 600 (Avg.) | 0 | SqM
| SIZE: 800 X 800 (Avg.) | 0 | SqM
| SIZE: 600 X 1200 (Avg.) | 0 | SqM
19 | MS FABRICATION WORK FOR REPAIR, JACKETING STRUCTURAL MEMBERS ETC. Providing and fixing MS fabrication work for repairs, jacketing, etc. as directed by engineer incharge including epoxy treatment etc. complete. | 1000 | SqM
20 | DOORS (WITHOUT FRAMES) Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws(including necessary handles, knobs, locks, tower bolt stopper etc. complete | 37.8 | SqM
21 | DOOR FRAMES Providing and fixing in position factory made precast RCC M-40 fixing with hold fast embedded in 1:3:6 concrete block for doors and windows frames having excellent smooth finish as per IS: 6523 with reinforcement of 3 Nos, 6 mm dia main bars tied with 3 mm M.S stirrups placed @ 200 mm C/C and 6 numbers high strength polymer blocks of required size for fixing hinges including providing 6 no specially designed M.S. galvanised sleeves for accommodating 6 mm dia fully threaded bolts for fixing hold fast on vertical members, providing suitable arrangement for receiving sliding door bolts and tower bolt etc. all complete, as per the direction of Engineer-in-charge. The frame shall be measured in running metre correct to two places of decimal. Door frame 125 mmx 60 mm | 25.2 | CuM
22 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) (high quality paint as approved by engineer incharge) Make: Royal High Grade or Equivalent etc. complete. | 1132.6443 | SqM
23 | LUSTRE PAINT Providing and applying lustre paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 0 | SqM
24 | MODULAR TABLES Providing and fixing modular tables of 18 mm moisture resistant with 1 mm laminate finish. The table top edge shall be post formed. Tops are supported on partition with the help of steel cantilevers. All work tops fixed at the standard anthropometric working height of 750mm from the ground level & finished with well filleted edges, thus making those users friendly. One circular hole for computer cables to be provided with Stainless Steel mat finish polish cable cap. Pedestal shall have castors at the base. Tables will have powder coated CPU trolley, articulated keyboard tray with pull out mouse tray. Including movable multi use pedestal/cabinet with drawer and file cabinet of size(400x700)mm will be provided with laminate finish. Color of laminate, texture and finish shall be approved by Engineer incharge of Embassy. All the accessories shall be as per detail drawing and design including fixture and fastening with polishing and finishing etc. complete. | 150 | No.s
25 | CHAIR Providing and supplying rolling, revolving, back rest, metal body chairs of Herman Millar or equivalent as approved by the engineer in-charge with installation etc. complete
|  | 450 | No.s
26 | CABINATES Providing and fixing cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete
| Conf. Rm1: 20.0 m (l) x 0.45 (w) x 3.0 (h). | 10 | No.s
27 | PARTITION Providing, supplying and fixing in position aluminium partitions in toilets, back stage area etc. with both sides laminated panels having frame made out of aluminium extruded tubular section of size 40 mm x 65 mm with 12 mm thick three layered flat pressed teak wood particle board bonded with BWP type exterior grade phenol formaldehyde synthetic resin conforming to I.S.12823-1990, laminated on both sides, Novateak or equivalent fixed with aluminium glazing clips of size 12mm x 12 mm as per approved drawing etc. complete.(Sample to be got approved from Engineer Incharge before use) | 50 | SqM
28 | FRAMELESS GLASS PARTITION Providing and fixing glass frameless partition in console room with 12 mm thick toughen glass with SS pure polyester and powder coated section as per drawings, design, frosting, Eonox or equivalent fittings, computer based edge polishing, silicon filling, glass film or approved make etc. complete | 25 | No.s
29 | GLASS DOORS Providing and fixing glass doors in 12 mm thick toughen glass with bottom door closer and lock of Hettich or Equivalent, SS Handle 30 Cm in square pattern in mat finish, Eonox or equivalent fitting with glass film of approved make and micron etc. complete. (Glass Brand Saint- Gobain/Modigaurd/Equivalent) | 25 | No.s
30 | SITTING IN ENTRANCE LOBBY Providing and supplying three seater sitting stool with approved make and model by Engineer Incharge | 4 | No.s
31 | DISPLAY RACK IN ENTRANCE LOBBY Providing and fixing wall mounted display rack as per design in entrance lobby in 18 mm marine ply (Greenply/Kitply/Or equivalent brand) with ISO certification with 12 mm toughen glass with lighting system for illumining objects form inside with all necessary accessories etc. complete. | 4 | No.s
32 | ART WORK IN ENTRANCE LOBBY AND OTHER PLACES Providing and supplying art work as directed by engineer in charges, focus/spot/LED or any type of lighting as per drawing and specifications etc. complete | 4 | No.s
33 | POWDER COATED ALLUMINUM LOUVERED WINDOWS Providing and fixing in position powder coated aluminium louvered windows of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 10.8 | SqM
34 | POWDER COATED ALLUMINUM LOUVERED VENTILATORS IN TOILETS Providing and fixing in position powder coated aluminium louvered ventilators of various sizes as per detailed drawings and specifications including aluminium frames 80 x 38 mm box type 5 mm thick sheet glass louvers, clips / rubber plain P.V.C. gaskets of approved quality etc. Complete. Note: Contractor shall approve sample from Engineer in-charge | 4.32 | Nos
35 | EXTERIOR PAVING IN GREY STONE SLABS Providing and fixing exterior paving in grey stone slab on the existing foot path by keeping openings for drainage, making ramp, step, planter etc. complete. | 10 | SqM
36 | EXTERIOR PAVING IN RECKLI TILES Providing, manufacturing and fixing Reckli tiles for exterior paving by use of Polyutherine model of Reckli - Germany insitu casting in M20 concrete as per the instruction of Engineer etc. complete | 10 | SqM
37 | REPAIR OF ENTRANCE PORTCH Repair of entrance porch by water proofing in bitumen with tile finish on top surface (as per water proofing specifications), replacement of old drainage with new drainage system, including painting, re concreting the floor etc. complete | 1 | LS
38 | PANTRY PLATFORM Providing and fixing pantry platform in traditional Indian design in front of auditorium entry as approved by architect or engineer in Corian and MR 18mm play with internal lighting, glass work etc. complete | 0 | LS
39 | CABINATE IN PANTRY Providing and fixing 3.2 m (l) x 0.45 (w) x 3.0 (h) cabinet in 18 mm MR ply, partly as show case and partly as cabinet with 1 mm thick internal & external laminate (texture or Glassy or Plain) with 8 mm glass including all fittings, doors, handle, hinges all Hettich or equivalent as approved by architect including internal lighting etc. complete | 0 | LS
40 | EXTERIOR CEMENT PLASTER Providing and applying 20 mm thick external sand faced plaster in cement mortar 1:3 at all heights and locations in one coat for masonry (except stone masonry) and concrete surfaces including racking out joints, hacking of concrete surface, watering, finishing, curing, scaffolding etc. complete. | 250 | LS
41 | EXTERIOR PAINT Providing and supplying exterior water proof paint of high quality weather proof with base coat of approved material, including scrapping and making old surfaces, scaffolding etc. complete | 150 | No.s
42 | EXTERNAL BRICK TILES WORKS Providing and fixing brick tiles on old and new surfaces including removal of the tiles on damaged surfaces. This include scaffolding, providing necessary finish, labor etc. complete | 150 | No.s
43 | METAL CLIP IN CEILING Providing and fixing Gl Clip in Metal Ceiling System of 600x600 mm module which includes providing and fixing 'C' wall angle of size 20x30x20 mm made of 0.5 mm thick pre painted steel along the perimeter of the room with help of nylon sleeves and wooden screws at 300 mm center to centre, suspending the main C carrier of size 10x38x10 mm made of G.I steel 0.7 mm thick from the soffit with help of soffit cleat 37x27x25x1.6 mm, rawl plugs of size 38x12 mm and C carrier suspension clip and main carrier bracket at 1000 mm c/c. Inverted triangle shaped Spring Tee having height of 24 mm and width of 34 mm made of Gl steel 0.45 mm thick is then fixed to the main C carrier and in direction perpendicular to it at 600 mm centers with help of suspension brackets. Wherever the main C carrier and spring T have to join, C carrier and spring T connectors have to be used. All sections to be galvanized @ 120 gms/sqm (both side inclusive), fixing with clip in tiles into spring T with : | 468.1875 | SqM
GI Metal Ceiling Clip in plain Bevelled edge global white color tiles or color as approved by engineer of size 600x600 and 0.5 mm thick with 25 mm height, made of G I sheet having galvanizing of 100 gms/ sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted etc. complete (Make: Armstrong/Hunter Douglas or equivalent)
44 | FALSE CEILING IN CORIAN SOLIDS Providing and fixing false ceiling on ground floor ceiling with circular shape and in periphery of the baffle system with aluminium pipe supports and marine ply base for taking two 6 mm double Corian Solid sheet with proper anchored, connecting, positing, polishing etc. complete | 5 | No.s
45 | POP FALSE CEILING Providing and fixing false ceiling in Mezzanine and other areas of 12 mm thick of fibrous plaster of Paris which includes G.I. Perimeter channel ( MF6) of size 0.40 mm thick (having one flange of 20 mm and another flange of 30 mm and web of 27 mm) along with perimeter of ceiling, screw fixed to brick wall , concrete surface, partition with the help of nylon sleeves and screws at 610 mm centres. Thereafter suspending G.I. intermediate channel ( MF 7) 600 mm. C/C of size 45mm (0.9 mm thick with two flanges of 15 mm each) from the soffit at 450 mm centre with connecting angle (ie ceiling angle) of width 25mm x 10mm x 0.40mm thick fixed to soffit with G.I.cleat and steel expansion fasteners. Celling sections ( MF 5 ) of 0.55 mm thickness having knurled web of 51.5 mm and two flanges of 26 mm each with lips of 10.5 mm are then fixed to the intermediate channel with the help of connecting clip and in direction perpendicular to the intermediate channel at 450 mm centres. | 396.76 | SqM
12.5 mm tapered edge is then screw fixed to celling section with dry wall Sqm 612.00 248.00 screws at 230 mm centres. Screw fixing is to be done mechanically with suitable attachment. The boards are to be joined and finished so as to have flush look which includes filling and finishing the tapered & square edges of the boards with jointing compound, joint paper tape and appropriate suitable primer and three coats of oil bound distemper . The item includes for light fitting, grill diffusers and cut out etc. have to be made with frame of perimeter channels of size 20mm x 30mm x 0.55mm.thick supported suitable and angle bead is to be used at steps to get straight line finish etc. complete. This also include making wooden/ ply decoration as per drawing by using CNC cutting with LED background light with glass etc. complete as directed by Engineer- in-charge
46 | FALSE CEILING ( 600 X 600 BOARD) Providing and fixing false ceiling of 15 mm thickness Acoustic tabular Armstrong / Everest / AMS / Aerolite or equivalent (0.6x0.6m) boards of approved make, with shapes and sizes as per drawings including powder coated G.I .wall angle of 20mmx20mm size ,G.I. grid runners of size 15mmx 38mm at 600mmcenter to centre both ways and suspended using G.I. wire 3mm wire including fixing using butter fly clips and fasteners including transporting , scaffolding, all necessary labour and machinery , finishing etc complete. (as directed by Engineer In Charge).sample to be got approved from Engineer Incharge before execution of work | 2 | No.s
47 | ACOUSTIC WALL PANELS IN WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete. | 1074.788 | SqM
48 | WOODEN STAGE Providing and supplying wooden stage with approved quality teak wood sections and planks as per drawings and instruction of engineer incharge. (Drawing No. 07 ) | 2 | No.s
49 | STAGE BACK DROP Providing and supplying wooden wall panel with approved quality teak wood plan and sections with in vertical wall upto ceiling height including scaffolding, internal light and its cable arrangement etc. complete. | 2 | No.s
50 | 86" (INTERACTIVE TEACHING SMART BOARD) Product Code: TR3DJ TR3DJ Series Brightness: 350nits Multi Touch Point: 20 Points (Max.) Interface : HDMI (3), RGB (1), Audio In (1), RS-232C In (1), RJ45 (1), USB 3.0 Type A (3), USB 2.0 Type A (3), Audio Out / Optical Output, Touch USB (2) 4k Resolution 20 Point Multi Touch Anti-glass, Tempered Glass Screen Mirroring Minimal Air Gap Integrated Speaker and Wi-Fi Module Smooth Touch & Writing Experience Easy connection & sharing User friendly experience Make: LG 75 TR3DJ or Equivalent | 2 | No.s
51 | LECTURE HALL PROJECTOR Providing supply, installation and commissioning large-venue projector combines a laser light source and 3LCD technology for powerful, uncompromising images ideal for events staging and auditoriums with extraordinary color brightness, 3LCD projectors with brilliant images, delivering 6,000 lumens or more of color brightness and 6,000 or more lumens of white brightness1, laser light engine 3 years guarantee, connectivity to all equipments, with extra powered lenses, including, installation, cabling, remote, and screen proposed hal etc. complete (Make: Epson Pro L1100U or equivalent) | 2 | No.s
52 | LECTURE HALL WHITE BOARD Providing and fixing magnetic white board of the size 6 m x 4.5 m or more in approved material and quality with TW case border of more than 20 cm thick with arrangement of pens, duster, and supplying 4 set of four color pens and two dusters etc. complete | 2 | No.s
53 | LECTURE HALL PODIUM Providing and supplying lecture hall podium as per the approved design in marine ply with 1.0 to 1.5 mm approved texture laminate with glass work, electrical works etc. complete | 2 | No.s
54 | PROJECTOR SCREEN Providing and supplying projector screen of size 6 m x 4.5 m or more with manual closing system in approved material and quality etc. complete | 2 | No.s
TOTAL

## TRR UT
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: LECTURE HALLS IN UTILITY AND ACDEMIC BLOCKS AND RENOVATIONS OF LABORATORIES
BOQ FOR TERRACE FLOOR
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMMOUNT IN FIGURE | AMOUNT IN WORDS
1 | DISMANTLING AND CLEANING BROKEN DEBRIS Dismantling and cleaning all necessary debris including transportation to necessary location as local rules. This include housekeeping for keeping area clean etc. complete | 2135.04 | CuM
2 | ANTI-TERMITE TREATMENT Providing Pre-constructional anti-termite treatment conforming to IS-6313 (part II) using chloropyrifos EC 20 Emulsion or equivalent of 1% concentration by weight for creating barrier under and all around basement excavation, backfill in immediate contact with foundation and treating the top surface along the external perimeter of building, expansion joints, surrounding of pipes, water conduits and at places suggested and as directed by Engineer-In-Charge covering 10 years guaranty. | 151.2 | SqM
3 | BRICK WORK Brick work with common bricks of class designation 7.5 in Cement mortar 1:6 (1 cement : 6 coarse sand) | 35 | CuM
4 | WATER PROOF CEMENT PAINT Providing and applying two coats of waterproof cement paint of an approved make and colour as per manufacturers specifications to smooth sand faced or other surfaces, upto 10m height from ground level and at all locations as directed including preparing surfaces for painting by any approved means, watering, scaffolding, cleaning and curing etc. complete as directed by Engineer-in-charge. | 6.25 | SqM
5 | UPVC PIPES AND BENDS Providing and fixing UV resistant self fit UPVC pipes of approved make for Rainwater down takes confirming to IS 13592:1992 Type A suitable for 4kg/sqcm pressure for following pipe diameters including rain water receiving recess with pvc plug bend necessary fittings such as offsets shoes, fixing the pipes on wall with clips filling the joints with solvent/cement and necessary scaffolding etc. complete as directed by Engineer In Charge. 150mm dia | 150 | Rmt
6 | WATER PROOFING TO TERRACE Providing water proofing treatment of Old Terraces by removing existing treatment. Sealing of cracks by non shrink cracks fill compound by applying first coat of polymer modified semi-viscous paste prepared by mixing polymer of approved make (such as Aquatek conchem/ Master Seal 550/brush bond / RoffSupercrete/ Webercrete/ Monobond / Perma shield / Hypercrate / Master Crete M 81/ MC-Bauchemie) and Cement in 1:2proportion ( 1 litre polymer : 2 Kg Cement) or Rohnex water proofing system in two coats(1kg powder,700 ml water and polymer jelly for first coat & 1 kg powder,500 ml water & polymer jelly for second coat) to a neatly cleaned and dust free concrete surface and upto 300 mm over parapet wall prepared by removing loose and deposited material with brush and water, laying glass fibre mesh of 10 x 10 specification of approved make over tacky surface of first coat of polymer followed by second coat in transverse direction, laying mechanical protective cover to polymer coating treatment with brick bat coba with burnt broken brick bats laid in C.M. 1:5 admixed with approved water proofing compound, filling up to half depth of brick bats, curing this layer for 3 days, | 2.5 | Sq.M
applying cement slurry over this layer joints of brick bats with C.M. 1:3 admixed making the Sq.m. 1102.00 219.00 junctions at the parapet rounded and tapered top for required height, with drip mould at the junction of plaster and parapet and curing and covering 7 years Guarantee against leak proofness on court including ponding test etc. complete (Make: Dr. Fixit Roofseal or equivalent)
7 | GROUTING TO VARIOUS PARTS Providing Grouting by specially prepared grout of Weber Crete /Roff Supercrete /Polyalk P/Monobond /Perma shield/Hypercrate or equivalent with cement in proportion 1:3.5 (1 part chemical & 3.5 part cement by weight) along with 50 ml super plasticizer Roff Plast 320/sun polycrete NCT/Perma Plast/Supercon 100 or non shrinking, non cracking antiwash high strength polymer cement grout P C grout available in bags or equivalent with proper water for injectable consistency and applying it in the body of structure like slab, beam, column, pillars, deckslab, retaining wall, basement, underground and elevated water storage reservoir concrete and brick wall, crack portion of structure etc. by injectng method, to achieve its original strength including drilling of suitable diameter drills holes at 2 to 4 Nos. per sqm. using caps and nozzle grouting machinery necessary, scaffolding, finishing and covering gurantee of 10 years and necessary testing etc. complete. | 100 | Kg
8 | EMULSION PAINT Providing and applying plastic emulsion paint on old and new surfaces of approved quality, colour and shade to surfaces in two coats including scaffolding and preparing the surfaces (excluding the primer coat) complete. | 150 | SqM
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## ELE UT
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: LECTURE HALLS IN UTILITY AND ACDEMIC BLOCKS AND RENOVATIONS OF LABORATORIES
BOQ FOR ELECTRICAL WORK FOR ALL FLOORS
Sr.No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | POINT WIRING FOR INDEPENDENT PLUG Providing, fixing and testing point wiring for independent plug in 20 mm rigid PVC conduit with 1.5 sqm FRLS grade Copper wire with modular switch and concealed wiring with necessary joints, and required accessories complete. As directed by Engineer in-charge | 47 | No.s
2 | LIGHT POINT WITH SINGLE MODULER SWITCH Providing, fixing and testing light point with single modular switch with concealed cables and modular plate etc. complete. | 44 | No.s
3 | POINT WIRING FOR WALL MOUNTED FANS Providing, fixing and testing point wiring for wall mounted fans in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade Copper wire with flush type switch and required accessories etc. complete. | 26 | No.s
4 | CEILING FANS Providing, supplying and fixing ceiling fans of with regulator and all other accessories, etc. complete (Make: Bajaj or equivalent) | 20 | No.s
5 | CONCEALED SQUARE LED LIGHT FIXTURE Supply, Installation, testing & commissioning of the 2x36 watt, 2x2” size concealed light fixture as per drawings complete with LED system etc. (Make: Philips: Green Square 39W 2x2 LED Light or equivalent) with switches etc. | 30 | No.s
6 | LED BATTEN LIGHTS Supply, Installation, testing & commissioning of the 36 watt or above, concealed LED circular light fixture in console room complete with copper choke, starter, LED etc. (Make PHILIPS Mirolta Pro r16 36 Watts LED Batten - High Power High Performance Tube Light - Cool Day Light or equivalent) | 28 | No.s
7 | CEILING CIRCULER LIGHT PANEL Supply, installation, testing & commissioning of white color ceiling fixture of material metal and glass with 15 watt or above LED light including, started, LED system, switches etc, complete (Make: Philips myLiving canvas white model no. 77050/31/16 or equivalent) | 12 | No.s
8 | STEPS AND RAMP LIGHTING Supply, Installation, testing & commissioning for steps in auditorium, steps, below seats and ramp lighting of the watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania: wall 5 STE DIR 4W LED WHT LLB with switches etc. | 50 | No.s
9 | PENDENT LIGHT IN LOBBY Providing, installation, testing & commissioning of 6-1/2’’ Pendalyte with Satined Aluminium Reflector, with suspended, lamp holder, LED/CFL lamp of 32 watt and above etc. complete (Make: Philips Pendalyte with Satined Aluminium Reflector or equivalent) | 10 | No.s
10 | HANGING LIGHT FIXTURES FIXTURE Supply, Installation, testing & commissioning hanging light fixtures in lotus shape made from brass of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested
| Large | 1 | No.s
| Small | 1 | No.s
11 | WALL LED LIGHT Providing, supplying, installation as commissioning, regular 26 watt and above light fixtures with light holder of approved quality including concealed cabling, modular switch, texted as approved by engineer, with wiring, scaffolding, etc. complete (PHILIPS 26-watt LED Bulb ¦AceBright High Wattage LED Bulb Base: B22 Light Bulb for Home ¦ Crystal White or equivalent) | 2 | No.s
12 | WALL MOUNTED FIXTURE Supply, Installation, testing & commissioning for curved wall in console room of approved watt, concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. as per design suggested | 2 | No.s
13 | LED TUBE ON TERRACE Supply, installation, testing and commission of LED tube25 watt or above of material glass and plastic including bulb, clips, LED system, civil work etc complete(Make: Philips Linea 26-Watt LED Tube (White) or equivalent) | 3 | No.s
14 | LED STRIP LIGHTS Supply, installation, testing and commissioning of LED strip lights 8 watt above per metre of required color or hue including, adaptor, controller, male-female clips, cable, switches etc. complete in ceiling, tables, with scaffolding, glass etc. complete. (Make: Philips 800284 Hue Light strip Plus, 2Nd Generation or equivalent) | 25 | Rmt
15 | EXTERIOR LED LIGHTS FOR BUILDING Supply, Installation, testing & commissioning for lights in exterior in elevation of LED or compliance concealed mounted light fixture complete with copper choke, starter, tube etc. make Havells/Sylvania/Philips with switches etc. Contractor shall assign specialised company for design and installation of external lighting with previous experience in similar field. Contractor and subcontractor shall approve the design for external lighting from architect or engineer any suggestions shall be incorporated with all necessary requirement etc. complete This item include AMC for three years.. | 0 | No.s
16 | POINT WIRING FOR LAN POINTS Point wiring for LAN points will be carried out with CAT 6, LAN Cable, in surface/ recessed existing PVC conduits, inclusive of p/f of G.I/ PVC box & modular plate RJ 45 AT&T LAN socket. Work includes cutting & repair of chase to original finish. (Make of cable: Polycap or equivalent) | 30 | No.s
17 | CIRCUIT WIRING Supply and wiring wall / floor etc. / recessed / surface as per colour code with the following size PVC Insulated copper wire along with given earth wire for phase neutral and earth conductor with standard colour coding, through ISI marked rigid PVC conduit of given size with all accessories. The rate includes the cost of complete wiring from switch box to switch box etc. complete (Make of wire: Polycap or equivalent)
a. | 2 x 1.0 Sqmm PVC Copper wire in 20 mm dia conduit for Emergency Stop Box Connection | 250 | Rmt
b. | 3 x 1.5 Sqmm PVC Copper wire with in 20 mm dia conduit (The rate includes the cost of complete wiring between individual switch boards) | 250 | Rmt
c. | 3 x 2.5 Sqmm PVC Copper wire with in 20 mm dia conduit (for lighting main circuit, 15A plug points & UPS point wiring & 1T AC) | 250 | Rmt
d. | 5 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 3-Ph circuits like 3-Ph AC / UPS) | 250 | Rmt
e. | 3 x 4 Sq.mm PVC Copper wire with in 20 mm dia conduit. (for 1.5/2Tonne AC and UPS I/P & O/P upto UPS O/P DB and for Sign Boards if there are multiple Name boards) | 250 | Rmt
18 | AC/HEATER METAL BOX Supplying and fixing for AC/Heater metal box of GI box with modular plate and cover in front on surface or in recess , including providing and fixing of 3 No's 3 pin 5/6 amps modular socket outlet and 15/16 amps. Modular switch, connections, painting etc. as required | 5 | No.s
19 | TWO WAY CONNECTIONS Point wiring for two way connects for switching lights in corridor, toilet, landscape, steps in 20 mm rigid PVC conduit with 1.0 sqm FRLS grade copper wire with flush type switch and required accessories. | 5 | No.s
20 | UTP NETWORK CABLE CAT 6 Supplying & installing UTP networking Cat-6+ cable suitable for LAN / WAN Computer networking. | 30 | No.s
21 | M. S. CABLE TRAY Fabrication and installing required sizes of perforated M.S. cable trays including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with M.S. suspenders and including painting with powder coating etc. as required. | 1 | No.s
22 | DISTRUBUTION BOARD Distribution board of approved make as per design requirements of Legrand or equivalent make with MCB cables, separation for computers, lights etc. complete | 2 | No.s
23 | PVC CABLE Supply and erecting PVC armoured cable 2 core 2.5 sq. mm stranded/solid copper conductors continuous 5.48 sq. mm (12 swg) GI earth wire complete erecting with glands & lugs on wall in trenches complete (Measurement to be as per site condition and location of Mains) (Make: Polycap or equivalent) | 300 | Rmt
24 | SUPPLY 16" EXHAUST FAN Supply of 16" exhaust fan of PVC of high speed with installation, testing including aluminium or wooden framing etc. complete. (Make Godrej/Philips or equivalent) Note: Contractor shall approve the make and model from Engineer in-charge of Embassy) | 6 | No.s
25 | BELL POINTS Providing and fixing bell points with concealed conduits with cable, bell of approved make, modular switches, etc. complete | 6 | No.s
26 | TELEPHONE POINTS Providing and fixing telephone points with modular plate, cable, switch with concealed cabling etc. complete | 20 | No.s
27 | EARTHLING WITH G.I. EARTH PIPE Earthling with G.I. earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but without charcoal or coke and salt) as required. | 25 | No.s
28 | MUSIC CUM PA SYSTEM OF PHILIPS MAKE Providing and fixing music systems of Philips make with speakers, CD, USB, Radio etc. complete as approved by engineer incharge with stereo speakers in appropriate locations, including stereo head phones etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. Design & product detail to be submitted with tender. | 4 | No.s
29 | MODULAR KITCHEN HOT PLATE Providing and fixing modular kitchen hot plate with 4 no. of coils of Philips or equivalent make etc. complete. Note: Contractor shall approve the make model of music systema and speaker from Engineer in-charge Embassy. | 0 | No.s
TOTAL
ACOUSTIC WALL PANELS IN AUDITORIUM WALLS Acoustic wall panels made in combination with cement tiles and perforated acoustic tile of required size. Cement tiles will be made of Reckli formliner of Polyutherine material. Tiles will be fixed with MS quire tube framing of 2" x 2" pipe at 2.0 M interval. Framing shall be sufficient to take load of the tiles. This include making joint, finishing, painting the tiles, etc. complete.

## AC SPLIT
NAME OF WORK: REDEVELOPMENT OF ACMS CAMPUS
NAME OF PROJECT: LECTURE HALLS IN UTILITY AND ACDEMIC BLOCKS AND RENOVATIONS OF LABORATORIES
BOQ FOR SPLIT AIR CONDITIONING WORKS
Sr. No. | Description of Work | Qty. | Rate | Per | AMOUNT IN FIGURE | AMOUNT IN WORDS
1 | HI-WALL SPLIT AIR CONDITIONER: Supply, Installation, Testing and Commissioning of Hi-Wall Split Air Conditioner, Inverter Type, Latest BEE Star Rating : 5 Star , Copper Condenser and Evaporator Coil, Eco-Friendly refrigerant, Operating on 1Φ, 50Hz, 230 Volts power supply, With inbuilt voltage stabilizer with operational range 180 to 260 Volts, Suitable for Indoor-Outdoor piping length not less than 20.0 Meters, Certified Operating Conditions 20 to 48 ⁰CDB and along with cordless remote control as per following cooling Capacities:
| Cooling Capacity: 12000 BTU/Hr | 4 |  | Each
| Cooling Capacity: 24000 BTU/Hr | 10 |  | Each
2 | CASSETTE AIR CONDITIONER: Supply, Installation, Testing and Commissioning of Cassette Air Conditioner, Inverter Type, Latest BEE Star Rating : 5 Star , Copper Condenser and Evaporator Coil, Eco-Friendly refrigerant, Operating on Single Phase, 50Hz, 230 Volts or 3-Phase power supply, Suitable for Indoor-Outdoor piping length not less than 20.0 Meters, Certified Operating Conditions 20 to 48 ⁰CDB and along with cordless remote control as per following cooling Capacities:
2.2 | Cooling Capacity: 42000 BTU/Hr | 1 |  | Each
3 | COPPER REFRIGERANT PIPING: Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed celle lastometric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required NOTE: 1) The Copper Piping & Piping Circuit should be with Minimum Number of joints, which shall be attained by : (i) Using One End Expanded Tubes (ii) Bending the tubes instead of using elbow joints wherever 90 degree bending is required. (2) Piping should be routed at site in such a manner, that brazed joints in the refrigeration piping are kept to a minimum. (3) The makes of tube fittings shall be same as that of tubes.(4) The thickness of fittings used shall be same as that of the pipe.
3.1 | 6.4 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 75 |  | Rmt
3.2 | 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 115 |  | Rmt
3.3 | 12.7 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 75 |  | Rmt
3.4 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 115 |  | Rmt
3.5 | 19.0 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 1 |  | Rmt
4 | DRAIN PIPE (RIGID uPVC): Supply and complete fixing of rigid uPVC pipe of following sizes for drain water piping connections of VRF cassette type indoor units including required fittings and Supports duly insulated with 6 mm thick closed cell crosslinked polyethylene (XLPE) tubular insulation Make: ISI mark or any reputed make with prior approval of engineer.
4.1 | Nominal Dia. Size: 32.0 mm | 75 |  | Meter
4.2 | Nominal Dia. Size: 25.0 mm | 75 |  | Meter
5 | CABLE TRAYS: Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
| 300 mm width X 62.5 mm depth X 2.0 mm thickness | 25 |  | Rmt
6 | REFRIGERANT CHARGING FOR TOP UP IN HI WALL SPLIT/CASSETTE TYPE AIR CONDITIONER: Supply, Charging and Testing of additional R-410a/R-32 gas charging in split/Cassette Air conditioner as per standard procedure recommended by Air Conditioner manufacturer and complete as required. | 15 |  | Kg
7 | POWER CABLE FOR AIR CONDITIONER: Supply, Laying and Testing of 4 core x 4.0 Sq. mm PVC round sheathed, copper conductor Industrial cable for voltage grade upto 1100 Volts as per IS694:1990 in Dia.20.0 mm uPVC (Heavy size) conduit pipe complete as required for air conditioner as per installation guidelines given by air conditioner manufacturer.
7.1 | Size: 4 core x 4.0 Sq. mm | 75 |  | Rmt
7.2 | Size: 4 core x 2.5 Sq. mm | 150 |  | Rmt
8 | MS FABRICATED STAND: Supply of MS fabricated stand duly painted with two coat of red oxide paint followed by two coat of Black enamel paint and should be suitable for the installation of VRF system as per approved design and drawing. | 100 |  | KG
9 | DISMANTLING AND SHIFTING OF HI WALL SPLIT AIR CONDITIONER (Cooling Capacity: 2.0 TR): Dismantling and shifting of Hi wall Split air conditioner of following capacity as per standard pracitice recommended by the AC manufacturer includes required pump down operation for the recovery of refrigerant, dismantling of Indoor-Outdoor unit, complete copper piping and electrical wiring, Base plate of ID Unit and mounting stand of OD unit, Shifting of dismantled material as per instructions of Engineer, at any location of institute premises. | 2 |  | Each
10 | WALL MOUNTING STAND/BRACKET: Supply and Fixing of Wall Mounting Stand made up of Heavy Duty GI sheet (Thickness: 2.0 MM), Powder Coated, along with required fitting material such as Screws, Anchors, Fasteners etc complete as required. | 15 |  | Each
Total